## Sheet1
Fault 2022-02-11 15:03:35
Fault Number | Building Trade | Trade Category | Type of Fault | Impact | Location | Cancel Status | Reported Date | Fault Acknowledged Date | Responded on Site Date | RA Conducted Date | Work Started Date | Work Completed Date | Attended By | Action(s) Taken | Other Trades Required Date | Cost Cap Exceed Date | Assistance Requested Date | Fault Reference | End User Priority | Incident Report | Remarks
FID7038 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1065 |  | 2022-01-31 23:54:02 | 2022-02-01 08:44:09 | 2022-02-01 08:44:50 | 2022-02-01 08:45:18 | 2022-02-01 08:45:51 | 2022-02-01 08:46:52 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID7037 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Nursing Stn D |  | 2022-01-31 23:32:54 | 2022-02-01 08:48:00 | 2022-02-01 08:49:31 | 2022-02-01 08:50:11 | 2022-02-01 08:51:16 | 2022-02-01 08:53:08 | Vadivelu Balasubramanian | adjusted the temperature in bms setpoint 16to15 make it cool |  |  |  |  | 1 |  | Aircon make it cool-v.bala-low
FID7036 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-31 22:39:16 | 2022-02-01 08:06:25 | 2022-02-01 08:06:44 | 2022-02-01 08:07:11 | 2022-02-01 08:07:32 | 2022-02-01 08:11:18 | FRC | adjusted temperature Aircon make it cool |  |  |  |  | 1 |  | Aircon make it cool-v.bala-low
FID7029 | Plumbing & Sanitary | Kitchen Drain Pipe | Other: sound coming | Localised to room | RMG > RH > 8 > Stn B Corridor |  | 2022-01-31 15:27:00 | 2022-01-31 17:30:53 | 2022-01-31 17:31:13 | 2022-01-31 17:31:32 | 2022-01-31 17:31:38 | 2022-01-31 17:33:42 | Muthu Shanmugavelu | Sound due to toilet flushing system faulty in room 825..Temperorily closed the supply valve and Informed engineer.. | [6 empty] | Sound coming from the pipe shaft-Shanmu-low
FID7028 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Business Centre |  | 2022-01-31 14:55:57 | 2022-01-31 14:57:23 | 2022-01-31 14:57:54 | 2022-01-31 14:58:15 | 2022-01-31 14:58:46 | 2022-01-31 15:20:02 | FRC | Adjusted VAV 2-1-13 temperature setpoint from 20c to 22c and damper from 90% manual to 60% manual in bms system make it warm | [6 empty] | Aircon too cold, make it warm-Su-low
FID7027 | Medical Equipment | Fridges & Freezers | Alarm | Localised to room | RMG > RH > 7 > Lab Office |  | 2022-01-31 14:55:19 | 2022-02-07 14:35:59 | 2022-02-07 14:36:25 | 2022-02-07 14:36:44 | 2022-02-07 14:37:04 | 2022-02-07 14:37:49 | FRC | Fridge faulty, need to arrange the vendor to check. Pending. | [6 empty] | Medical fridge temperature high, showing 15c-Jailani-low
FID7024 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 7 > Operating Theatre 4 |  | 2022-01-31 13:28:43 | 2022-01-31 13:48:19 | 2022-01-31 13:48:37 | 2022-01-31 13:49:15 | 2022-01-31 13:53:00 | 2022-01-31 13:53:59 | Muthu Shanmugavelu | back to normal | [6 empty] | Medical gas panel alarming-Shanmu-medium
FID7021 | Plumbing & Sanitary | Water Heater | No water | Localised to room | RMG > RH > 8 > Ward 835 (Victoria Suite Guest Rm) |  | 2022-01-31 11:53:07 | 2022-02-07 14:39:04 | 2022-02-07 14:39:23 | 2022-02-07 14:39:44 | 2022-02-07 14:40:05 | 2022-02-07 14:40:35 | FRC | Checked and rectified | [6 empty] | Shower hot water take long time to be hot-ilayaraja-low
FID7020 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1017 |  | 2022-01-31 11:39:57 | 2022-01-31 15:28:03 | 2022-02-07 14:49:34 | 2022-02-07 14:49:59 | 2022-02-07 14:50:22 | 2022-02-07 14:51:04 | FRC | Manually close the air supply outlet slightly | [6 empty] | Aircon make it warm-Jailani-low
FID7019 | Building | Door Closer | Unable to open or close properly | Localised to room | RMG > RH > 1 > FCC |  | 2022-01-31 11:36:19 | 2022-02-07 14:46:50 | 2022-02-07 14:47:11 | 2022-02-07 14:47:30 | 2022-02-07 14:47:52 | 2022-02-07 14:48:24 | FRC | Repaired the door | [6 empty] | Door unable to open-Ming cai-low
FID7018 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Nursing Stn D |  | 2022-01-31 11:35:34 | 2022-02-07 14:31:58 | 2022-02-07 14:32:22 | 2022-02-07 14:32:43 | 2022-02-07 14:33:02 | 2022-02-07 14:34:58 | FRC | Checked and rectified | [6 empty] | Patient rooms shower water take long time to be hot, to check-ilayaraja-low
FID7013 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 8 > Stn D Corridor |  | 2022-01-31 10:03:51 | 2022-01-31 10:14:09 | 2022-01-31 10:15:31 | 2022-01-31 10:15:54 | 2022-01-31 10:16:24 | 2022-01-31 10:18:10 | Packiyaraj | Reset call bell system back to normal | [6 empty] | Nurse call time display not working-Packiyaraj-low
FID7012 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2022-01-31 10:03:03 | 2022-02-07 14:26:01 | 2022-02-07 14:27:06 | 2022-02-07 14:28:58 | 2022-02-07 14:29:41 | 2022-02-07 14:31:16 | FRC | Reduced AHU 13-4 VSD from 50% to 45% in bms system to reduce the airflow sound | [6 empty] | Airflow got sound-Satha-low
FID7005 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 967 - 968 |  | 2022-01-31 07:37:35 | 2022-01-31 08:35:01 | 2022-01-31 08:35:40 | 2022-01-31 08:36:01 | 2022-01-31 08:36:11 | 2022-01-31 08:36:50 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low
FID7004 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 967 - 968 |  | 2022-01-31 07:34:06 | 2022-01-31 08:23:32 | 2022-01-31 08:23:58 | 2022-01-31 08:24:26 | 2022-01-31 08:25:10 | 2022-01-31 08:26:42 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low
FID7002 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1057 |  | 2022-01-31 06:14:59 | 2022-02-07 14:08:40 | 2022-02-07 14:09:00 | 2022-02-07 14:09:23 | 2022-02-07 14:22:07 | 2022-02-07 14:24:15 | FRC | Adjusted the room vav temperature setpoint and damper position in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID7001 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2022-01-30 23:21:30 | 2022-02-07 13:55:20 | 2022-02-07 13:56:12 | 2022-02-07 13:56:36 | 2022-02-07 13:57:23 | 2022-02-07 13:57:57 | FRC | Adjusted the aircon temperature make it warm in bms system | [6 empty] | Aircon make it warm-aru-low
FID7000 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn B |  | 2022-01-30 23:18:55 | 2022-02-07 13:58:41 | 2022-02-07 13:59:09 | 2022-02-07 13:59:35 | 2022-02-07 13:59:56 | 2022-02-07 14:00:45 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6999 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > Lab Office |  | 2022-01-30 20:36:40 | 2022-01-30 20:39:28 | 2022-01-30 20:39:58 | 2022-01-30 20:40:23 | 2022-01-30 20:40:52 | 2022-01-30 20:41:47 | Vadivelu Balasubramanian | co2 big replaced 25 kg | [6 empty] | Need to change CO2 cylinder-v.bala-medium
FID6995 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1058 |  | 2022-01-30 18:27:50 | 2022-01-30 18:34:54 | 2022-01-30 18:35:35 | 2022-01-30 18:35:57 | 2022-01-30 18:36:43 | 2022-01-30 18:37:42 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm | [6 empty] | Aircon make it warm-v.bala-low
FID6994 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 8 > Business Centre |  | 2022-01-30 18:23:41 | 2022-01-30 18:38:36 | 2022-01-30 18:39:09 | 2022-01-30 18:39:43 | 2022-01-30 18:40:10 | 2022-01-30 18:42:17 | Vadivelu Balasubramanian | checked 849 oxygen relief back to normal | [6 empty] | Medical gas panel alarming-V.Bala-medium
FID6993 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2022-01-30 18:18:16 | 2022-02-04 12:46:58 | 2022-02-04 12:47:20 | 2022-02-04 12:47:41 | 2022-02-04 12:48:01 | 2022-02-04 12:48:46 | FRC | reset back to normal | [6 empty] | TV channel not working-a.bala-low
FID6992 | Mechanical | Mechanical Ventilation | Noisy | Localised to room | RMG > RH > 7 > Operating Theatre 12 |  | 2022-01-30 18:12:50 | 2022-01-30 18:28:54 | 2022-01-30 18:43:46 | 2022-01-30 18:44:25 | 2022-01-30 18:48:26 | 2022-01-30 18:54:48 | Vadivelu Balasubramanian | adjusted temperature setpoint noise reduces bake to normal | [6 empty] | Sound coming from the ceiling, air flow very strong-v.bala-low
FID6991 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 8 > NICU |  | 2022-01-30 18:05:01 | 2022-02-04 12:49:26 | 2022-02-04 12:49:46 | 2022-02-04 12:50:05 | 2022-02-04 12:50:26 | 2022-02-04 12:51:04 | FRC | replaced new light bulb | [6 empty] | Light flickering-a.bala-low
FID6988 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 918 |  | 2022-01-30 15:07:29 | 2022-01-30 15:11:46 | 2022-01-30 15:28:13 | 2022-01-30 15:30:59 | 2022-01-30 15:31:57 | 2022-01-30 15:33:18 | Arasan Balasubramanian | reset back to normal | [6 empty] | Call bell ringing-a.bala-low
FID6987 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > Nuclear Med PET/CT |  | 2022-01-30 11:55:37 | 2022-01-30 11:56:45 | 2022-01-30 11:57:02 | 2022-01-30 11:57:22 | 2022-01-30 11:57:39 | 2022-01-30 11:58:16 | FRC | replaced new light bulb |  |  |  |  | 1 |  | Light flickering-A.Bala-low
FID6984 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RH > 10 > Ward 1040 |  | 2022-01-30 09:29:55 | 2022-01-30 13:05:56 | 2022-01-30 13:06:26 | 2022-01-30 13:06:48 | 2022-01-30 13:07:19 | 2022-01-30 13:08:04 | Vadivelu Balasubramanian | toilet bowl choke clear |  |  |  |  | 1 |  | Toilet choke-V.Bala-low
FID6982 | Building | Door Lock | Unable to open or close properly | Localised to room | RMG > RH > 10 > Ward 1017 |  | 2022-01-30 08:21:53 | 2022-02-07 14:01:30 | 2022-02-07 14:01:50 | 2022-02-07 14:03:36 | 2022-02-07 14:04:00 | 2022-02-07 14:04:27 | FRC | Repaired the door handle | [6 empty] | Door handle spoilt-aru-low
FID6980 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 818 |  | 2022-01-30 07:25:45 | 2022-02-07 14:05:02 | 2022-02-07 14:05:24 | 2022-02-07 14:05:44 | 2022-02-07 14:06:05 | 2022-02-07 14:07:51 | FRC | Manually adjusted the damper open onsite | [6 empty] | Aircon make it cool-aru-low
FID6975 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-29 21:11:32 | 2022-02-07 13:46:37 | 2022-02-07 13:46:59 | 2022-02-07 13:47:35 | 2022-02-07 13:47:58 | 2022-02-07 13:49:10 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6972 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1337-1343 |  | 2022-01-29 20:37:30 | 2022-01-29 20:39:19 | 2022-01-30 13:09:18 | 2022-01-30 13:09:41 | 2022-01-30 13:10:10 | 2022-01-30 13:11:00 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm | [6 empty] | Aircon too cold, make it warm-v.bala-low
FID6966 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Business Centre Office 1 |  | 2022-01-29 16:24:15 | 2022-02-07 13:44:07 | 2022-02-07 13:44:28 | 2022-02-07 13:44:49 | 2022-02-07 13:45:28 | 2022-02-07 13:46:04 | FRC | Manually open the damper onsite |  |  |  |  | 1 |  | Aircon make it cold-packiyaraj-low
FID6965 | Mechanical | Gas System | Missing | More than 1 room | RMG > RH > 9 > Ward 971 - 972 |  | 2022-01-29 16:21:14 | 2022-01-29 19:50:38 | 2022-01-29 19:50:57 | 2022-01-29 19:51:22 | 2022-01-29 19:51:41 | 2022-01-29 19:52:11 | Chang Fook Keong Alan | I have fixed back the item |  |  |  |  | 1 |  | Vacuum suction bar missing-allan-low
FID6964 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1059 |  | 2022-01-29 16:15:50 | 2022-01-29 16:36:27 | 2022-01-29 16:36:49 | 2022-01-29 16:37:09 | 2022-01-29 16:37:30 | 2022-01-29 16:38:56 | FRC | adjusted the temprature Aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-a.bala-low
FID6960 | Building | Partition Wall | Chipped / Cracked | More than 1 room | RMG > RH > 10 > Ward 1048 |  | 2022-01-29 14:34:17 | 2022-01-29 19:52:40 | 2022-01-29 19:52:59 | 2022-01-29 19:53:30 | 2022-01-29 19:53:48 | 2022-01-29 19:54:39 | Chang Fook Keong Alan | I have Stick back the wallpaper |  |  |  |  | 1 |  | Wallpaper came off-Allan-low
FID6958 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn D |  | 2022-01-29 14:12:39 | 2022-01-29 14:18:02 | 2022-01-29 14:18:19 | 2022-01-29 14:18:38 | 2022-01-29 14:18:59 | 2022-01-29 14:20:14 | FRC | adjusted the temprature Aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-a.bala-low
FID6955 | Electrical | Call System | Other: not working | Localised to room | RMG > RH > 8 > Ward 851 |  | 2022-01-29 13:49:11 | 2022-01-31 08:44:04 | 2022-01-31 08:44:43 | 2022-01-31 08:45:03 | 2022-01-31 08:45:27 | 2022-01-31 08:46:07 | Packiyaraj | Reset back to normal | [6 empty] | Call bell not working-packiyaraj-low
FID6953 | Plumbing & Sanitary | Shower Fittings | Leaking | Localised to room | RMG > RH > 7 > ICU Rm 703 |  | 2022-01-29 12:11:49 | 2022-01-29 19:55:41 | 2022-01-29 19:56:00 | 2022-01-29 19:56:18 | 2022-01-29 19:56:37 | 2022-01-29 19:57:57 | Chang Fook Keong Alan | What are leaking and stop | [6 empty] | Water leaking from the shower-Allan-low
FID6952 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Skin & Aesthetics Waiting Area |  | 2022-01-29 11:40:00 | 2022-01-29 19:58:40 | 2022-01-29 19:59:00 | 2022-01-29 19:59:20 | 2022-01-29 19:59:39 | 2022-01-29 20:00:09 | Chang Fook Keong Alan | Has made it back back to normal | [6 empty] | Aircon noisy-Allan-low
FID6949 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 8 > Business Centre |  | 2022-01-29 11:01:58 | 2022-01-29 12:35:39 | 2022-01-29 12:36:13 | 2022-01-29 12:36:36 | 2022-01-29 12:36:57 | 2022-01-29 12:38:41 | Hossain | Onsite check & found there is no alarm got everything is normal. | [6 empty] | medical gas panel alarming-Hossain-medium
FID6948 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Ward 851 |  | 2022-01-29 10:59:52 | 2022-02-07 11:53:58 | 2022-02-07 11:54:17 | 2022-02-07 11:54:36 | 2022-02-07 11:55:11 | 2022-02-07 13:43:07 | FRC | Checked and rectified | [6 empty] | No hot water-Hossain-low
FID6946 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > NICU |  | 2022-01-29 10:29:30 | 2022-02-07 11:46:28 | 2022-02-07 11:50:31 | 2022-02-07 11:52:17 | 2022-02-07 11:52:37 | 2022-02-07 11:53:12 | FRC | Checked and rectified | [6 empty] | Basin tap no hot water-Ming Cai-low
FID6945 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 2 > Raffles Chinese Medicine Clinic |  | 2022-01-29 10:02:33 | 2022-01-29 13:22:19 | 2022-01-29 13:22:40 | 2022-01-29 13:22:59 | 2022-01-29 13:24:13 | 2022-01-29 13:27:09 | FRC | replaced new call system | [6 empty] | Call bell not working-A.bala-low
FID6944 | Medical Equipment | Hygrometer | Other: need to replace battery | Localised to room | RMG > RH > 7 > Angio Technical / Store Rm |  | 2022-01-29 10:01:30 | 2022-01-31 15:06:37 | 2022-01-31 15:06:58 | 2022-01-31 15:07:17 | 2022-01-31 15:07:35 | 2022-01-31 15:08:02 | Chang Fook Keong Alan | I have replace new battery | [6 empty] | Need to replace hygrometer battery-Allan-low
FID6943 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2022-01-29 09:59:56 | 2022-01-29 12:40:11 | 2022-01-29 12:40:39 | 2022-01-29 12:42:14 | 2022-01-29 12:42:33 | 2022-01-29 13:10:16 | Hossain | Onside check & found room was warm due VAV actuator valve was closed. open the actuator valve 70% & monitor back to normal. | [6 empty] | Aircon make it cool-Hossain-low
FID6942 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 9 > Ward 910 |  | 2022-01-29 09:58:46 | 2022-01-31 08:31:17 | 2022-01-31 08:32:00 | 2022-01-31 08:32:35 | 2022-01-31 08:32:57 | 2022-01-31 08:33:47 | Packiyaraj | Replaced bulb | [6 empty] | Bed head light flickering-Packiyaraj-low
FID6941 | Electrical | Call System | Other: Call bell keep ringing | Localised to room | RMG > RH > 9 > Ward 918 |  | 2022-01-29 09:57:44 | 2022-01-31 08:34:44 | 2022-01-31 08:35:13 | 2022-01-31 08:36:24 | 2022-01-31 08:37:13 | 2022-01-31 08:38:30 | Packiyaraj | Reset back to normal | [6 empty] | Call bell keep ringing-Packiyaraj-low
FID6940 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RSC > 9 > Internal Med Waiting Area A |  | 2022-01-29 09:55:20 | 2022-01-29 13:30:44 | 2022-01-29 13:31:04 | 2022-01-29 13:31:23 | 2022-01-29 13:31:47 | 2022-01-29 13:32:28 | FRC | reset back to normal | [6 empty] | TV not working-A.bala-low
FID6936 | Medical Equipment | Warming Cabinet | Alarm | Localised to room | RMG > RH > 7 > OT |  | 2022-01-28 17:52:56 | 2022-02-07 11:40:30 | 2022-02-07 11:40:52 | 2022-02-07 11:41:14 | 2022-02-07 11:41:34 | 2022-02-07 11:44:18 | FRC | Checked onsite, power socket not working. Informed to electrical team to follow up. Replaced new twin socket | [6 empty] | Solution blanket warmer not working-Ming Cai-low
FID6933 | Plumbing & Sanitary | Tap | Other: No hot water | Localised to room | RMG > RH > 8 > NICU |  | 2022-01-28 17:25:00 | 2022-01-28 17:27:08 | 2022-01-28 17:27:31 | 2022-01-28 17:27:53 | 2022-01-28 17:28:21 | 2022-01-28 17:29:38 | Muthu Shanmugavelu | Explained staff need to open and wait for a while..after got hot water on the tap.. | [6 empty] | Basin tap not hot-Shanmu-low
FID6932 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 8 > Ward 851 |  | 2022-01-28 17:23:42 | 2022-01-28 17:56:03 | 2022-01-28 17:56:36 | 2022-01-28 17:59:53 | 2022-01-28 18:01:10 | 2022-01-28 18:02:28 | Rajendran Manikandan | Reset normal back | [6 empty] | Safe box cannot close-Mani-low
FID6931 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1059 |  | 2022-01-28 17:22:29 | 2022-02-07 11:23:09 | 2022-02-07 11:24:46 | 2022-02-07 11:27:26 | 2022-02-07 11:27:46 | 2022-02-07 11:29:00 | FRC | Adjusted vav 1-1-17 temperature setpoint from 28c to 24c and damper position from 0% manual to auto (20%) in bms system make it cool slightly. | [6 empty] | Aircon make it cool-Su-low
FID6930 | Plumbing & Sanitary | Shower Fittings | Damaged / Loose / Cracked | Localised to room | RMG > RH > 9 > Business Centre Office 2 |  | 2022-01-28 16:54:45 | 2022-01-28 19:28:07 | 2022-01-28 19:28:28 | 2022-01-28 19:29:02 | 2022-01-28 19:29:54 | 2022-01-29 14:32:28 | Hossain | Replaced the shower head back to normal. | [6 empty] | Need to replace new shower head-Hossain-low
FID6929 | Mechanical | Pneumatic Tube | Missing | Localised to room | RMG > RH > 2 > RM@RH |  | 2022-01-28 16:53:37 | 2022-01-28 16:56:42 | 2022-01-28 16:56:58 | 2022-01-28 16:58:03 | 2022-01-28 16:58:26 | 2022-01-28 17:00:57 | FRC | checked in the pneumatic tube system, lab send the tube wrongly to A&E. Called A&E staff to return back the tube to RMRH. | [6 empty] | Pneumatic tube missing-Su-low
FID6928 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1055 |  | 2022-01-28 16:52:33 | 2022-01-28 16:55:13 | 2022-01-28 16:55:30 | 2022-01-28 16:55:47 | 2022-01-28 16:56:03 | 2022-01-28 17:01:51 | FRC | Adjusted VAV 1-1-20 temperature setpoint to 28c and damper to 0% manual in BMS system make it warm | [6 empty] | Aircon make it warm-Su-low
FID6927 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2022-01-28 16:50:22 | 2022-01-28 18:04:30 | 2022-01-28 18:05:06 | 2022-01-28 18:05:48 | 2022-01-28 18:06:15 | 2022-01-28 18:06:59 | Rajendran Manikandan | Replaced new telephone cable | [6 empty] | Telephone not working-mani-low
FID6926 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 11 > Facilities Dept. |  | 2022-01-28 16:07:34 | 2022-01-31 08:47:36 | 2022-01-31 08:47:59 | 2022-01-31 08:48:47 | 2022-01-31 08:49:31 | 2022-01-31 08:50:35 | Packiyaraj | Replaced telephone wire | [6 empty] | Telephone (ext 1667) not working properly-Packiyaraj-low
FID6925 | Building | Wall | Other: Wallpaper peel off | Localised to room | RMG > RH > 2 > Raffles Japanese Clinic |  | 2022-01-28 16:06:28 | 2022-02-07 11:19:01 | 2022-02-07 11:20:04 | 2022-02-07 11:20:28 | 2022-02-07 11:20:51 | 2022-02-07 11:21:30 | FRC | Glue back the wallpaper | [6 empty] | Wallpaper peel off-Nazri-low
FID6924 | Office and Furniture | Safe Box | Cannot operate / defective | Localised to room | RMG > RH > 8 > Ward 851 |  | 2022-01-28 16:05:01 | 2022-02-07 11:16:50 | 2022-02-07 11:17:11 | 2022-02-07 11:17:32 | 2022-02-07 11:17:53 | 2022-02-07 11:18:21 | FRC | Replaced new battery for safe box | [6 empty] | need to replace safe box battery-packiyaraj-low
FID6922 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 6 |  | 2022-01-28 15:14:46 | 2022-01-28 15:15:43 | 2022-01-28 15:16:45 | 2022-01-28 15:17:06 | 2022-01-28 15:17:36 | 2022-01-28 16:15:53 | FRC | Adjusted the temperature setpoint from 26c to 22c and heater position from 80% manual to auto (0%) in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6920 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 9 > Ward 916 |  | 2022-01-28 14:48:47 | 2022-01-28 15:35:09 | 2022-01-28 15:35:45 | 2022-01-28 15:36:15 | 2022-01-28 15:36:37 | 2022-01-28 15:37:12 | Packiyaraj | Replaced bulb | [6 empty] | Toilet mirror light fused-Packiyaraj-low
FID6919 | Building | Wall | Other: Signage | Affecting Public | RMG > RH > 7 > Passenger Lift Lobby |  | 2022-01-28 14:29:26 | 2022-02-07 11:14:12 | 2022-02-07 11:14:31 | 2022-02-07 11:14:51 | 2022-02-07 11:15:21 | 2022-02-07 11:15:56 | FRC | Fixed back the poster holder using double sided tape | [6 empty] | Poster holder dropped-Nazri-low
FID6918 | Plumbing & Sanitary | Scrub Sink | Other: Scrub sensor not working | Affecting Public | RMG > RH > 7 > OR7&8 Scrub Rm |  | 2022-01-28 13:46:16 | 2022-01-28 14:04:54 | 2022-01-28 14:05:13 | 2022-01-28 14:05:31 | 2022-01-28 14:05:40 | 2022-01-28 14:06:32 | Muthu Shanmugavelu | Adjusted the sensitivity and closed the loop with sister Chew.. now working normal | [6 empty] | Scrub sink sensor not working-Shanmu-low
FID6916 | Office and Furniture | Table | Other: no working | More than 1 room | RMG > RH > 7 > Day Surgery |  | 2022-01-28 12:56:48 | 2022-01-28 16:30:21 | 2022-01-28 16:30:53 | 2022-01-28 16:31:46 | 2022-01-28 16:32:22 | 2022-01-28 16:34:39 | Hossain | Onsite check & found patient trolley wheel is broken. Replaced the trolley wheel back to normal. | [6 empty] | Patient trolley broken-hossain-low
FID6915 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 16 > Eye Centre Consult Rm 2 |  | 2022-01-28 12:50:28 | 2022-02-07 11:10:51 | 2022-02-07 11:11:15 | 2022-02-07 11:11:35 | 2022-02-07 11:12:04 | 2022-02-07 11:13:13 | FRC | Adjusted VAV 16-2-5 temperature setpoint and damper position in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6914 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > Main Lobby |  | 2022-01-28 12:45:03 | 2022-01-28 16:03:50 | 2022-01-28 16:04:24 | 2022-01-28 16:04:57 | 2022-01-28 16:13:58 | 2022-01-28 16:14:56 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low
FID6913 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Angio Suite |  | 2022-01-28 12:19:46 | 2022-02-07 11:07:29 | 2022-02-07 11:07:51 | 2022-02-07 11:08:13 | 2022-02-07 11:08:39 | 2022-02-07 11:09:56 | FRC | Replaced new battery for hygrometer | [6 empty] | Need to replace new battery for hygrometer-aru-low
FID6912 | Mechanical | Autodoor | Other: Door stuck | Localised to room | RMG > RH > 7 > Operating Theatre 1 (Endoscopy) |  | 2022-01-28 12:08:25 | 2022-01-28 16:17:00 | 2022-01-28 16:17:37 | 2022-01-28 16:18:11 | 2022-01-28 16:23:10 | 2022-01-28 16:24:14 | Rajendran Manikandan | Auto door servicing and normal back | [6 empty] | Auto door stuck, open very slow-Mani-low
FID6911 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 8 > Children Centre |  | 2022-01-28 11:52:57 | 2022-02-07 11:04:29 | 2022-02-07 11:04:55 | 2022-02-07 11:05:17 | 2022-02-07 11:05:43 | 2022-02-07 11:06:49 | FRC | Adjusted VAV 8-4-11 temperature setpoint from 24c to 20c in bms system make it cool. Damper position automatically increase from 49% to 61% | [6 empty] | Aircon warm-Aru-low
FID6910 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 2 > RM@RH |  | 2022-01-28 11:50:49 | 2022-01-28 16:35:59 | 2022-01-28 16:36:42 | 2022-01-28 16:37:26 | 2022-01-28 16:38:29 | 2022-01-28 16:41:34 | Hossain | Cleared the choked back to normal. | [6 empty] | Basin choke-Hossain-low
FID6908 | Medical Equipment | CSSD Sterilisers | Alarm | Localised to room | RMG > RH > 7 > CSSD |  | 2022-01-28 11:18:59 | 2022-01-28 11:47:20 | 2022-01-28 11:47:38 | 2022-01-28 11:47:57 | 2022-01-28 11:49:05 | 2022-01-28 17:31:35 | Muthu Shanmugavelu | Getinge completed and sterliser 1 back to normal.. | [6 empty] | Steriliser 1 indicates 'steam gen. error'-Shanmu-low
FID6905 | Building | Ceiling | Leaking | Affecting Public | RMG > RH > 11 > Facilities Dept. |  | 2022-01-28 10:34:12 | 2022-01-28 16:42:54 | 2022-01-28 16:43:16 | 2022-01-28 16:43:36 | 2022-01-28 16:43:57 | 2022-02-07 11:03:40 | FRC | Checked and rectified | [6 empty] | Water leaking from ceiling-Hossain-low
FID6902 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1051 |  | 2022-01-28 09:54:19 | 2022-01-28 11:13:26 | 2022-01-28 11:14:04 | 2022-01-28 11:14:37 | 2022-01-28 11:15:03 | 2022-02-07 09:28:10 | Rajendran Manikandan | Temporary swop from room 1042 to 1050 TV done | [6 empty] | TV damaged, swap with 1043-Mani-low
FID6901 | Building | Door Lock | Unable to open or close properly | Localised to room | RMG > RH > 10 > Ward 1031 |  | 2022-01-28 09:53:10 | 2022-01-28 16:44:42 | 2022-01-28 16:45:02 | 2022-01-28 16:45:22 | 2022-01-28 16:45:31 | 2022-01-28 16:49:43 | Hossain | Onside check & found door unable to close due to door frame dislodge. adjusted the door frame & check back to normal. | [6 empty] | Door cannot lock-Hossain-low
FID6886 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > AHU Room |  | 2022-01-27 22:26:24 | 2022-01-27 22:43:50 | 2022-01-27 22:44:16 | 2022-01-27 22:45:23 | 2022-01-27 23:09:54 | 2022-01-27 23:28:21 | Muthu Sathasivam | adjusted the setpoint on bms and checked on site | [6 empty] | Aircon make it cool-satha-low
FID6879 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2022-01-27 18:10:03 | 2022-01-27 18:10:42 | 2022-01-27 18:11:01 | 2022-01-27 18:11:19 | 2022-01-27 18:12:00 | 2022-01-27 18:17:30 | FRC | Adjusted VAV 2-3-6 damper position from auto (20%) to 5% manual in BMS system. thermostat setting at 23.6c. | [6 empty] | Aircon make it warm-Su-low
FID6878 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Ward 919 |  | 2022-01-27 17:29:17 | 2022-02-07 10:59:34 | 2022-02-07 11:00:08 | 2022-02-07 11:00:34 | 2022-02-07 11:00:55 | 2022-02-07 11:02:32 | FRC | Manually open the damper onsite to make aircon cool | [6 empty] | Aircon make it cool-Aru-low
FID6876 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RSC > 12 > Rehab Ctr T18 |  | 2022-01-27 16:06:53 | 2022-02-07 10:56:55 | 2022-02-07 10:57:14 | 2022-02-07 10:57:33 | 2022-02-07 10:57:53 | 2022-02-07 10:58:45 | FRC | Repaired and adjusted the sliding door alignment | [6 empty] | Sliding door cannot close properly-Ming cai-low
FID6875 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn C |  | 2022-01-27 16:05:44 | 2022-02-07 10:53:49 | 2022-02-07 10:54:08 | 2022-02-07 10:54:30 | 2022-02-07 10:54:50 | 2022-02-07 10:56:05 | FRC | Adjusted VAV 2-1-22 temperature setpoint from 22c to 20c in bms system make it cool. Damper position automatically increase from 65.8% to 90% | [6 empty] | Aircon very warm-Su-low
FID6873 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 16 > Eye Centre Consult Rm 2 |  | 2022-01-27 16:04:43 | 2022-02-07 10:51:19 | 2022-02-07 10:51:40 | 2022-02-07 10:51:59 | 2022-02-07 10:52:18 | 2022-02-07 10:53:16 | FRC | Adjusted VAV 16-2-5 temperature setpoint from 24c to 21c and damper from 40% manual to 80% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6870 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 7 > Operating Theatre 2 (IVF) |  | 2022-01-27 15:52:01 | 2022-01-27 21:57:38 | 2022-01-27 21:57:56 | 2022-01-27 21:58:15 | 2022-01-27 21:58:33 | 2022-01-27 21:59:05 | liumingcai | replace | [6 empty] | Need to change CO2 cylinder-Ming Cai-high
FID6869 | Office and Furniture | Cabinet | Cannot open / close | Localised to room | RMG > RSC > 11 > Radiology |  | 2022-01-27 15:50:26 | 2022-01-27 18:19:58 | 2022-01-27 18:20:31 | 2022-01-27 18:21:15 | 2022-01-27 18:21:36 | 2022-01-27 18:24:45 | Hossain | Onsite found patient locker unable lock. Repaired the lock set back to normal. | [6 empty] | Patient locker cannot lock-Hossain-low
FID6866 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn B |  | 2022-01-27 15:07:34 | 2022-01-27 15:41:57 | 2022-01-27 15:42:27 | 2022-01-27 15:42:45 | 2022-01-27 15:43:40 | 2022-02-07 10:50:06 | FRC | Adjusted VAV 1-1-13 temperature setpoint from 24c to 21c in bms system make it cool. Damper position automatically increase from 20% to 90% | [6 empty] | Aircon warm-Su-low
FID6865 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 8 > Business Centre |  | 2022-01-27 15:06:33 | 2022-01-27 15:43:35 | 2022-01-27 15:43:54 | 2022-01-27 15:44:13 | 2022-01-27 15:44:32 | 2022-01-27 15:45:53 | Muthu Shanmugavelu | swapped the interface cable from 1st stage panel to 8 Buisness counter panel..now back to normal.. | [6 empty] | Medical gas panel alarming-Shanmu-medium
FID6863 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-27 14:07:31 | 2022-02-07 10:45:48 | 2022-02-07 10:46:12 | 2022-02-07 10:46:54 | 2022-02-07 10:47:14 | 2022-02-07 10:48:08 | FRC | Checked onsite, aircon is working normal. Temperature is 23.5c, informed to staff. | [6 empty] | Aircon make it cool-Jailani-low
FID6862 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 11 |  | 2022-01-27 14:06:28 | 2022-01-27 15:45:07 | 2022-01-27 15:45:27 | 2022-01-27 15:46:07 | 2022-01-27 15:46:31 | 2022-01-27 15:48:31 | FRC | Adjusted temperature setpoint from 22c to 18c and heater from 100% auto to 0% manual in BMS system make it cool | [6 empty] | Aircon make it cool-Su-low
FID6852 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 11 > Level 11 |  | 2022-01-27 10:50:18 | 2022-02-07 10:41:55 | 2022-02-07 10:42:34 | 2022-02-07 10:42:54 | 2022-02-07 10:43:15 | 2022-02-07 10:43:53 | FRC | Done the telephone patching and tracing. Telephone line working back to normal. | [6 empty] | Telephone line not working-mani-low
FID6847 | Mechanical | Autodoor | Other: Glass door open and close | Affecting Public | RMG > RSC > 19 > Level 19 |  | 2022-01-27 10:13:46 | 2022-01-27 15:22:05 | 2022-01-27 15:22:37 | 2022-01-27 15:23:08 | 2022-01-27 15:24:18 | 2022-01-27 15:29:45 | Rajendran Manikandan | Reset normal back | [6 empty] | Auto glass door open and close-Mani-low
FID6845 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1058 |  | 2022-01-27 10:01:26 | 2022-01-27 10:03:45 | 2022-01-27 10:05:37 | 2022-01-27 10:05:57 | 2022-01-27 10:06:30 | 2022-01-27 10:51:30 | FRC | adjusted VAV 1-1-19 damper position from 90% auto to 60% manual in BMS system to reduce the airflow | [6 empty] | Airflow too strong-Su-low
FID6844 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 8 > Business Centre |  | 2022-01-27 10:00:31 | 2022-01-27 20:05:54 | 2022-01-27 20:07:02 | 2022-01-27 20:07:26 | 2022-01-27 20:07:46 | 2022-01-27 20:08:44 | Hossain | onsite check & reset the panel back to normal. | [6 empty] | Medical gas panel alarm when door open-Hossain-medium
FID6841 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1058 |  | 2022-01-27 09:34:38 | 2022-01-27 09:43:01 | 2022-01-27 09:53:19 | 2022-01-27 09:53:59 | 2022-01-27 09:54:18 | 2022-01-27 10:03:11 | FRC | Adjusted VAV 1-1-19 temperature setpoint at 22c and damper position from 20% manual to auto (90%) in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6840 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1057 |  | 2022-01-27 09:33:39 | 2022-01-27 09:36:48 | 2022-01-27 09:41:06 | 2022-01-27 09:42:01 | 2022-01-27 09:42:27 | 2022-01-27 10:02:33 | FRC | Adjusted VAV 1-1-19 temperature setpoint at 22c and damper position from 20% manual to auto (90%) in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6839 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1076 -1079 (4 Bed) |  | 2022-01-27 09:32:53 | 2022-01-27 09:35:07 | 2022-01-27 09:35:30 | 2022-01-27 09:35:53 | 2022-01-27 09:36:17 | 2022-01-27 09:55:58 | FRC | Adjusted VAV 1-2-3 temperature setpoint from 21c to 23c and damper from 100% manual to 50% manual in bms system make it warm | [6 empty] | Aircon make it warm-su-low
FID6838 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 10 > Ward 1002 |  | 2022-01-27 09:26:27 | 2022-01-27 18:28:03 | 2022-01-27 20:10:38 | 2022-01-27 20:10:59 | 2022-01-27 20:11:06 | 2022-01-27 20:19:57 | Hossain | onsite check & found bidet spray hose was loose. tightened back properly the hose back to normal. | [6 empty] | Bidet spray leaking-Hossain-low
FID6836 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Ward 848 |  | 2022-01-27 08:41:31 | 2022-02-07 10:35:03 | 2022-02-07 10:39:38 | 2022-02-07 10:40:08 | 2022-02-07 10:40:30 | 2022-02-07 10:41:04 | FRC | Manually open the diffuser onsite make it cool |  |  |  |  | 1 |  | Aircon make it cool-jailani-low
FID6835 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1076 -1079 (4 Bed) |  | 2022-01-27 08:40:08 | 2022-01-27 08:42:29 | 2022-01-27 08:43:01 | 2022-01-27 08:44:03 | 2022-01-27 08:44:22 | 2022-01-27 08:45:28 | FRC | adjusted the temperature make it cold |  |  |  |  | 1 |  | Aircon make it cool-a.bala-low
FID6834 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | More than 1 room | RMG > RSC > 1 > Handicap Toilet |  | 2022-01-27 08:13:23 | 2022-02-07 10:32:35 | 2022-02-07 10:32:53 | 2022-02-07 10:33:13 | 2022-02-07 10:33:33 | 2022-02-07 10:34:01 | FRC | Replaced new bidet spray |  |  |  |  | 1 |  | Bidet spray leaking-v.bala-low
FID6832 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2022-01-27 03:58:18 | 2022-01-27 04:05:24 | 2022-01-27 04:05:49 | 2022-01-27 04:06:14 | 2022-01-27 04:06:37 | 2022-01-27 04:07:39 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6831 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-27 01:52:32 | 2022-01-27 04:08:33 | 2022-01-27 04:10:06 | 2022-01-27 04:10:34 | 2022-01-27 04:11:00 | 2022-01-27 04:12:06 | Vadivelu Balasubramanian | adjusted vav control in bms setpoint 22to24 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6829 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU |  | 2022-01-27 00:56:03 | 2022-01-27 04:13:05 | 2022-01-27 04:13:34 | 2022-01-27 04:14:00 | 2022-01-27 04:14:43 | 2022-01-27 04:17:38 | Vadivelu Balasubramanian | adjusted temperature in bms ahu 7-1 setpoint 15to17 make it warm | [6 empty] | Aircon make it warm-v.bala-low
FID6827 | Office and Furniture | Telephone | No dial tone / not connected | More than 1 room | RMG > RH > 13 > Ward 1337-1343 Nurse Station |  | 2022-01-26 23:51:37 | 2022-01-26 23:53:03 | 2022-01-26 23:53:55 | 2022-01-26 23:54:56 | 2022-01-26 23:56:23 | 2022-01-26 23:58:43 | Arasan Balasubramanian | replaced telephone cable phone back to normal |  |  |  |  | 1 |  | Telephone not working-A.Bala-low
FID6825 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1337-1343 |  | 2022-01-26 22:50:07 | 2022-01-27 04:18:48 | 2022-01-27 04:19:20 | 2022-01-27 04:19:50 | 2022-01-27 04:20:23 | 2022-01-27 04:21:41 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 24to22 make it cool |  |  |  |  | 1 |  | Aircon make it cool-v.bala-low
FID6824 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Ward 915 (Isolation Rm) |  | 2022-01-26 22:47:04 | 2022-01-27 04:22:36 | 2022-01-27 04:23:10 | 2022-01-27 04:23:41 | 2022-01-27 04:24:18 | 2022-01-27 04:27:39 | Vadivelu Balasubramanian | adjusted temperature in onside isolation room display setpoint 19to22 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6823 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 9 > Ward 915 (Isolation Rm) |  | 2022-01-26 20:08:39 | 2022-01-26 20:14:52 | 2022-01-26 20:18:33 | 2022-01-26 20:19:27 | 2022-01-26 20:19:55 | 2022-01-26 20:20:49 | Muthu Sathasivam | adjusted the setpoint and active heater | [6 empty] | Aircon make warm-satha-low
FID6822 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 711 |  | 2022-01-26 20:06:58 | 2022-01-26 20:12:24 | 2022-01-26 20:13:06 | 2022-01-26 20:13:33 | 2022-01-26 20:14:06 | 2022-01-26 20:22:02 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Aircon make warm-Satha-low
FID6821 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1026 |  | 2022-01-26 20:05:15 | 2022-01-26 20:10:49 | 2022-01-26 20:11:15 | 2022-01-26 20:11:52 | 2022-01-26 20:12:15 | 2022-01-26 20:23:24 | Muthu Sathasivam | system working adjusted the thermostat by user | [6 empty] | Aircon make warm-Satha-low
FID6820 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Passenger Lift Lobby |  | 2022-01-26 18:08:17 | 2022-01-27 08:47:29 | 2022-01-27 08:47:57 | 2022-01-27 18:37:47 | 2022-01-27 18:38:11 | 2022-01-27 18:38:48 | Packiyaraj | Replaced driver | [6 empty] | Light flickering-Packiyaraj-low
FID6819 | Building | Door Knob / Handle | Other: Door handle loose | Localised to room | RMG > RSC > 8 > Children Centre Consult Rm 3 |  | 2022-01-26 18:05:45 | 2022-01-27 20:21:06 | 2022-01-27 20:21:40 | 2022-01-27 20:22:09 | 2022-01-27 20:22:29 | 2022-01-27 20:24:17 | Hossain | onsite check & found room 3 door handle came off. Fixed back the door handle accordingly. | [6 empty] | Door handle come out-Hossain-low
FID6817 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > RCM Dispensary |  | 2022-01-26 17:45:56 | 2022-02-07 10:29:30 | 2022-02-07 10:29:51 | 2022-02-07 10:30:15 | 2022-02-07 10:30:36 | 2022-02-07 10:31:25 | FRC | Adjusted VAV 5-1-16 temperature setpoint to 23c and damper from 70% manual to 50% manual in bms system make it warm slightly. | [6 empty] | Aircon too cold, make it warm-Satha-low
FID6812 | Medical Equipment | Patient Bed | Other: cannot operate | Localised to room | RMG > RH > 13 > Ward 1365-1370 |  | 2022-01-26 16:47:39 | 2022-02-07 10:26:22 | 2022-02-07 10:27:47 | 2022-02-07 10:28:06 | 2022-02-07 10:28:29 | 2022-02-07 10:28:56 | FRC | Repaired the bed | [6 empty] | Bed not working-Nazri-low
FID6811 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 7 |  | 2022-01-26 16:45:51 | 2022-02-07 10:21:03 | 2022-02-07 10:21:23 | 2022-02-07 10:21:42 | 2022-02-07 10:22:10 | 2022-02-07 10:22:46 | FRC | Adjusted the temperature setpoint to 28c and heater to 100% manual in bms system make it warm | [6 empty] | Aircon make it warm to 21c-Su-low
FID6810 | Building | Door Lock | Unable to open or close properly | Localised to room | RMG > RH > 4 > Carpark Store 1 (near SC1) |  | 2022-01-26 16:44:34 | 2022-01-26 17:25:26 | 2022-02-07 10:23:37 | 2022-02-07 10:24:34 | 2022-02-07 10:24:55 | 2022-02-07 10:25:35 | FRC | Door key missing, need to break open the door lock. Waiting for user confirmation before proceeding. | [6 empty] | Door cannot open, key missing-Ilayaraja-low
FID6808 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Nursing Stn D |  | 2022-01-26 15:54:49 | 2022-02-07 10:16:22 | 2022-02-07 10:17:15 | 2022-02-07 10:17:38 | 2022-02-07 10:17:58 | 2022-02-07 10:20:14 | FRC | Checked onsite the aircon is working normal and diffuser is fully open. Temperature is 19.2c onsite. Informed to sister in charge | [6 empty] | Aircon very warm-Jailani-low
FID6807 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2022-01-26 15:53:08 | 2022-01-26 16:40:27 | 2022-01-26 16:42:03 | 2022-01-26 16:43:10 | 2022-02-07 10:12:42 | 2022-02-07 10:14:26 | FRC | Analog telephone some buttons faulty. Replaced with spare phone. | [6 empty] | telephone button '2' not working-Packiyaraj-low
FID6801 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RH > 11 > Level 11 |  | 2022-01-26 14:36:58 | 2022-01-26 15:58:26 | 2022-01-26 18:49:21 | 2022-01-26 18:51:28 | 2022-01-26 18:52:44 | 2022-01-26 18:54:21 | Sivalingam Ilayaraja | cleared the chock | [6 empty] | Floor trap choke-Ilayaraja-low
FID6799 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 7 > OT |  | 2022-01-26 14:15:19 | 2022-02-07 10:09:11 | 2022-02-07 10:09:31 | 2022-02-07 10:09:50 | 2022-02-07 10:10:09 | 2022-02-07 10:10:37 | FRC | Replaced 1 big CO2 cylinder | [6 empty] | Need to replace 1 big CO2 cylinder-Allan-medium
FID6797 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 852 |  | 2022-01-26 13:34:09 | 2022-01-31 15:00:47 | 2022-01-31 15:01:36 | 2022-02-07 10:05:48 | 2022-02-07 10:06:08 | 2022-02-07 10:08:32 | FRC | Manually open the damper onsite to make it cool | [6 empty] | Aircon not cold-Jailani-low
FID6796 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1076 -1079 (4 Bed) |  | 2022-01-26 13:31:35 | 2022-01-26 13:31:56 | 2022-01-26 13:32:13 | 2022-01-26 13:32:30 | 2022-01-26 13:32:49 | 2022-01-31 14:51:43 | FRC | Adjusted VAV 1-2-3 temperature setpoint from 24c to 21c and damper position from auto (90%) to 100% manual make it cool | [6 empty] | Aircon make it cool-Su-low
FID6795 | Office and Furniture | Cabinet | Cannot open / close | Affecting Public | RMG > RH > 8 > Ward 809 |  | 2022-01-26 13:14:59 | 2022-01-27 09:05:27 | 2022-01-27 09:08:46 | 2022-01-27 09:09:05 | 2022-01-27 09:09:24 | 2022-01-27 09:09:47 | liumingcai | open | [6 empty] | Need to open student locker-Ming cai-low
FID6791 | Mechanical | Lift & Escalators (Schindler) | System Shows fault / Error code | Affecting Public | RMG > RH > 1 > FCC |  | 2022-01-26 12:01:09 | 2022-01-31 14:47:41 | 2022-01-31 14:48:01 | 2022-01-31 14:49:21 | 2022-01-31 14:49:42 | 2022-01-31 14:50:14 | FRC | Informed to schindler technician to check. Rectified | [6 empty] | Lift supervisory panel alarm cannot stop-Li Fei-low
FID6790 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 10 > Ward 1071 |  | 2022-01-26 12:00:11 | 2022-01-31 14:44:45 | 2022-01-31 14:45:05 | 2022-01-31 14:45:39 | 2022-01-31 14:46:12 | 2022-02-07 10:01:49 | FRC | Replaced new light | [6 empty] | Toilet ceiling light flickering-Nazri-low
FID6789 | Mechanical | Lift & Escalators (Schindler) | Other: Lift out of order | Affecting Public | RMG > RH > 12 > Level 12 |  | 2022-01-26 11:58:27 | 2022-01-26 13:35:53 | 2022-01-26 13:36:16 | 2022-01-26 13:36:51 | 2022-01-26 13:37:12 | 2022-01-26 13:38:09 | Chang Fook Keong Alan | #have check No one Stuck Inside | [6 empty] | Visitor Lift 5 stuck-Allan-low
FID6788 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > Nuclear Med Counter |  | 2022-01-26 11:57:21 | 2022-01-26 12:19:28 | 2022-01-26 12:20:10 | 2022-01-26 12:20:32 | 2022-01-26 12:20:49 | 2022-01-26 12:22:02 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6781 | Electrical | Socket | Misaligned / dangling | Affecting Public | RMG > RH > 2 > Dental Surgery 13 |  | 2022-01-26 11:04:55 | 2022-01-26 12:22:48 | 2022-01-26 12:24:10 | 2022-01-26 12:25:06 | 2022-01-26 12:25:27 | 2022-01-26 12:26:07 | Packiyaraj | fix back power point | [6 empty] | Power socket loose-Packiyaraj-low
FID6779 | Building | Ceiling Board Access Panel | Other: Drop | Affecting Public | RMG > RH > 2 > Dental Surgery 13 |  | 2022-01-26 10:51:20 | 2022-01-26 13:38:44 | 2022-01-26 13:39:03 | 2022-01-26 13:39:23 | 2022-01-26 13:39:45 | 2022-01-26 13:40:21 | Chang Fook Keong Alan | Have to replace new ceiling bored | [6 empty] | Ceiling board dropped-Allan-low
FID6778 | Plumbing & Sanitary | Soap Dispenser | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 7 > Level 7 |  | 2022-01-26 10:50:05 | 2022-01-31 14:41:46 | 2022-01-31 14:42:10 | 2022-01-31 14:43:07 | 2022-01-31 14:43:26 | 2022-01-31 14:43:58 | FRC | Hanged the sanitizer on the wall. | [6 empty] | Need to hang the hand sanitizer on the wall-Nazri-low
FID6777 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 2 > RIPC Waiting Area |  | 2022-01-26 10:34:56 | 2022-01-26 12:26:48 | 2022-01-26 12:27:20 | 2022-01-26 12:28:05 | 2022-01-26 12:28:28 | 2022-01-26 12:29:00 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6774 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 7 > OT |  | 2022-01-26 09:56:13 | 2022-01-27 20:26:46 | 2022-01-27 20:27:16 | 2022-01-27 20:27:37 | 2022-01-27 20:27:58 | 2022-01-27 20:28:50 | Hossain | Replaced the co2 cylinder as per request. | [6 empty] | Need to replace 1 big CO2 cylinder-Hossain-medium
FID6770 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Healthcheck Waiting Area |  | 2022-01-26 09:30:46 | 2022-01-26 09:35:45 | 2022-01-26 09:36:08 | 2022-01-26 09:36:31 | 2022-01-26 09:36:55 | 2022-01-26 09:44:13 | FRC | Adjusted vav 2-1-11 temperature setpoint from 24c to 21c and damper at 100% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6768 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Healthcheck Admin Office |  | 2022-01-26 09:29:23 | 2022-01-26 09:31:35 | 2022-01-26 09:32:03 | 2022-01-26 09:32:35 | 2022-01-26 09:32:59 | 2022-01-26 09:43:19 | FRC | Adjusted vav 1-1-19 temperature setpoint from 24c to 22c and damper position from 50% to 80% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6767 | Mechanical | Autodoor | Other: Auto door sometimes open and close | Affecting Public | RMG > RH > 8 > Nursing Stn B |  | 2022-01-26 09:28:19 | 2022-01-31 13:53:52 | 2022-01-31 13:58:53 | 2022-01-31 13:59:21 | 2022-01-31 13:59:42 | 2022-01-31 14:01:45 | FRC | Auto door safety sensor faulty. Need to arrange vendor to check, temporary lock the door and inform to staff and FCC. pending | [6 empty] | Auto door sometimes open and close-packiyaraj-low
FID6766 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 11 > Inpatient Pharmacy |  | 2022-01-26 09:26:33 | 2022-01-31 14:02:29 | 2022-01-31 14:10:00 | 2022-01-31 14:11:15 | 2022-01-31 14:11:35 | 2022-01-31 14:39:36 | FRC | Adjusted the vav onsite to make it cool | [6 empty] | Aircon make it cool-Jailani-low
FID6762 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 2 > RM@RH Consult Rm 3 |  | 2022-01-26 08:08:04 | 2022-01-31 13:42:39 | 2022-01-31 13:44:05 | 2022-01-31 13:45:03 | 2022-01-31 13:47:06 | 2022-01-31 13:47:42 | FRC | Adjusted the aircon temperature make it cool in bms system | [6 empty] | Aircon make it cold-Jailani-low
FID6761 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 12 > RHS Female Toilet |  | 2022-01-26 07:53:54 | 2022-01-26 08:01:44 | 2022-01-26 08:02:11 | 2022-01-26 08:02:32 | 2022-01-26 08:02:55 | 2022-01-26 08:03:48 | FRC | replaced new light bulb |  |  |  |  | 1 |  | Light fused-A.Bala-low
FID6760 | Plumbing & Sanitary | Basin / sink | Leaking | More than 1 room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-26 07:47:36 | 2022-01-31 11:56:49 | 2022-01-31 11:57:14 | 2022-01-31 11:59:10 | 2022-01-31 11:59:31 | 2022-01-31 11:59:56 | FRC | Checked and rectified |  |  |  |  | 1 |  | Water leaking from the basin-V.Bala-low
FID6759 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Stn D Corridor |  | 2022-01-26 04:14:00 | 2022-01-26 04:15:37 | 2022-01-26 04:15:56 | 2022-01-26 04:16:16 | 2022-01-26 04:16:41 | 2022-01-26 04:17:47 | FRC | adjusted the temperature Aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-A.bala-low
FID6758 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Rm 705 |  | 2022-01-26 02:04:46 | 2022-01-26 07:25:28 | 2022-01-26 07:26:04 | 2022-01-26 07:26:37 | 2022-01-26 07:27:08 | 2022-01-26 07:28:35 | Vadivelu Balasubramanian | adjusted temperature in bms setpoint 16to15 make it cool |  |  |  |  | 1 |  | Aircon make it cool-v.bala-low
FID6757 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2022-01-26 02:02:59 | 2022-01-26 07:29:47 | 2022-01-26 07:30:28 | 2022-01-26 07:31:08 | 2022-01-26 07:31:39 | 2022-01-26 07:32:38 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6750 | Building | Door Lock | Chipped / Cracked | Localised to room | RMG > RH > 2 > RM@RH Consult Rm 2 |  | 2022-01-25 19:54:21 | 2022-01-27 09:11:38 | 2022-01-27 09:11:56 | 2022-01-27 09:12:14 | 2022-01-27 09:12:32 | 2022-01-27 09:13:07 | liumingcai | repair | [6 empty] | Door lock need to replace-ming cai-low
FID6748 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-25 19:52:02 | 2022-01-25 19:57:17 | 2022-01-25 19:57:43 | 2022-01-25 19:58:05 | 2022-01-25 19:58:38 | 2022-01-25 20:09:04 | Muthu Sathasivam | adjusted the temperature | [6 empty] | Aircon make cool-satha-low
FID6747 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 853 |  | 2022-01-25 19:49:38 | 2022-01-25 20:09:43 | 2022-01-25 20:10:10 | 2022-01-25 20:11:08 | 2022-01-25 20:11:58 | 2022-01-25 20:12:57 | Muthu Sathasivam | open the damper manually | [6 empty] | Aircon make cool-satha-low
FID6746 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Women Centre |  | 2022-01-25 19:48:05 | 2022-01-26 10:16:21 | 2022-01-26 10:16:39 | 2022-01-26 10:17:07 | 2022-01-26 10:17:48 | 2022-01-26 10:18:26 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6740 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 8 > Labour Ward |  | 2022-01-25 17:57:44 | 2022-01-25 18:31:54 | 2022-01-25 18:32:13 | 2022-01-25 18:32:34 | 2022-01-25 18:32:55 | 2022-01-25 18:33:48 | Muthu Shanmugavelu | Reset back to normal | [6 empty] | Oxygen panel showing high alarm-Shanmu-medium
FID6739 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-25 17:11:31 | 2022-01-26 10:19:18 | 2022-01-26 10:19:28 | 2022-01-26 10:19:56 | 2022-01-26 10:20:25 | 2022-01-26 10:21:01 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6738 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1030 |  | 2022-01-25 17:10:40 | 2022-01-31 10:51:08 | 2022-01-31 10:51:32 | 2022-01-31 10:52:25 | 2022-01-31 10:52:50 | 2022-01-31 10:53:36 | FRC | Adjusted the room vav temperature setpoint and damper position in bms system make it warm | [6 empty] | Aircon make it warm-Su-low
FID6737 | Plumbing & Sanitary | WC / Squatting Pedestal | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2022-01-25 17:08:53 | 2022-01-27 09:13:44 | 2022-01-27 09:14:02 | 2022-01-27 09:14:19 | 2022-01-27 09:14:37 | 2022-01-27 09:15:06 | liumingcai | repair | [6 empty] | Toilet seat cover come out-ming cai-low
FID6735 | Mechanical | AHU UV Lights | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2022-01-25 16:10:11 | 2022-01-25 16:11:39 | 2022-01-25 16:11:56 | 2022-01-25 16:12:13 | 2022-01-25 16:12:29 | 2022-01-25 16:15:18 | FRC | Adjusted the vav 1-2-4, 1-2-5 and 1-2-6 temperature setpoint from 24c to 21c in bms system make it cool | [6 empty] | Aircon make it cool-Su-low
FID6734 | Electrical | Socket | Tripped / Short-Circuit / Overloaded | Localised to room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-25 16:07:53 | 2022-01-26 12:51:54 | 2022-01-26 12:52:16 | 2022-01-26 12:52:39 | 2022-01-26 12:53:00 | 2022-01-26 12:53:53 | Packiyaraj | Reset RCCB Back to normal | [6 empty] | Power socket no power-Packiyaraj-high
FID6732 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1022 |  | 2022-01-25 15:41:25 | 2022-01-25 15:41:42 | 2022-01-25 15:41:58 | 2022-01-25 15:42:18 | 2022-01-25 15:42:35 | 2022-01-25 16:13:58 | FRC | Adjusted vav 2-2-19 damper position from 90% manual to auto (20%) in bms system make it warm. thermostat setting at 29.9c | [6 empty] | Aircon make it warm-Su-low
FID6731 | Electrical | Socket | Tripped / Short-Circuit / Overloaded | More than 1 room | RMG > RH > 13 > Soiled Utility Rm |  | 2022-01-25 15:21:58 | 2022-01-25 16:03:14 | 2022-01-25 16:04:53 | 2022-01-25 16:29:41 | 2022-01-25 17:05:08 | 2022-01-25 18:11:30 | Sivalingam Ilayaraja | reset the main rcp then back to normal | [6 empty] | Power socket no power-ilayaraja-high
FID6730 | Electrical | Socket | Tripped / Short-Circuit / Overloaded | More than 1 room | RMG > RH > 13 > Ward 1345-1350 |  | 2022-01-25 15:20:57 | 2022-01-31 10:54:31 | 2022-01-31 10:55:09 | 2022-01-31 10:55:29 | 2022-01-31 10:55:50 | 2022-01-31 10:56:48 | FRC | Power trip. Reset the power back to normal | [6 empty] | Power socket no power-ilayaraja-high
FID6729 | Electrical | Socket | Tripped / Short-Circuit / Overloaded | More than 1 room | RMG > RH > 13 > Ward 1365-1370 |  | 2022-01-25 15:19:46 | 2022-01-31 11:01:57 | 2022-01-31 11:02:20 | 2022-01-31 11:02:39 | 2022-01-31 11:02:58 | 2022-01-31 11:03:28 | FRC | Reset the RCCB back to normal | [6 empty] | Power socket no power-ilayaraja-high
FID6728 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2022-01-25 15:14:40 | 2022-01-25 15:15:39 | 2022-01-25 15:16:09 | 2022-01-25 15:16:26 | 2022-01-25 15:16:42 | 2022-01-31 11:10:08 | FRC | Adjusted the aircon temperature in bms system make it cool | [6 empty] | No aircon-Su-low
FID6725 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Ward 996 - 999 (Serology Lab) |  | 2022-01-25 14:42:23 | 2022-01-31 11:15:20 | 2022-01-31 11:15:43 | 2022-01-31 11:16:04 | 2022-01-31 11:16:25 | 2022-01-31 11:17:09 | FRC | Adjusted the vav damper position to 100% fully open to make it cool. Temperature reduce slightly. | [6 empty] | Aircon warm-Jailani-low
FID6724 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 8 > Labour Ward Counter |  | 2022-01-25 14:41:41 | 2022-01-31 11:11:22 | 2022-01-31 11:12:20 | 2022-01-31 11:12:59 | 2022-01-31 11:13:25 | 2022-01-31 11:13:57 | FRC | Adjusted the aircon temperature make it cool in bms system | [6 empty] | Aircon make it cool-Jailani-low
FID6722 | Mechanical | Fire Protection System | System Shows fault / Error code | WIthin Building | RMG > RH > 1 > FCC |  | 2022-01-25 14:23:22 | 2022-01-25 14:23:44 | 2022-01-25 14:24:01 | 2022-01-25 14:24:19 | 2022-01-25 14:24:37 | 2022-01-25 14:40:33 | Muthu Shanmugavelu | Gib replaced new batteries for main panel and mimic panel at Fcc | [6 empty] | Gib replacing batteries for main panel and master mimic at Fcc-Shanmu-low
FID6721 | Plumbing & Sanitary | Flush Button | Water flowing non-stop | Localised to room | RMG > RH > 12 > Raffles Executive Medical Centre |  | 2022-01-25 14:14:45 | 2022-01-27 09:16:09 | 2022-01-27 09:16:26 | 2022-01-27 09:17:18 | 2022-01-27 09:17:36 | 2022-01-27 09:18:08 | liumingcai | repair | [6 empty] | Toilet flushing non stop-Ming cai-low
FID6720 | Building | Door Closer | Unable to open or close properly | Localised to room | RMG > RH > 8 > Ward 821 |  | 2022-01-25 14:13:08 | 2022-01-25 14:24:10 | 2022-01-25 14:26:54 | 2022-01-25 14:49:54 | 2022-01-25 14:51:14 | 2022-01-25 14:52:57 | Sivalingam Ilayaraja | done | [6 empty] | Door cannot open-ilayaraja-low
FID6718 | Building | Floor | Other: Carpet come out | Affecting Public | RMG > RH > 1 > Bed Lift Lobby |  | 2022-01-25 13:28:04 | 2022-01-31 11:53:50 | 2022-01-31 11:54:30 | 2022-01-31 11:54:52 | 2022-01-31 11:55:13 | 2022-01-31 11:55:41 | FRC | Fixed the carpet | [6 empty] | Carpet come out-ming cai-low
FID6716 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 11 > Inpatient Pharmacy |  | 2022-01-25 11:59:31 | 2022-01-31 11:44:54 | 2022-01-31 11:45:16 | 2022-01-31 11:45:37 | 2022-01-31 11:46:03 | 2022-01-31 11:52:16 | FRC | Adjusted the vav onsite to make it cool | [6 empty] | Aircon too warm-Jailani-low
FID6712 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Housekeeping Office |  | 2022-01-25 11:11:36 | 2022-01-25 11:27:31 | 2022-01-25 12:05:28 | 2022-01-25 12:05:50 | 2022-01-25 12:05:59 | 2022-01-25 12:06:29 | Packiyaraj | Replaced bulb | [6 empty] | Light flickering-packiyaraj-low
FID6710 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 10 > Doctor's Lounge |  | 2022-01-25 10:25:17 | 2022-01-25 12:07:10 | 2022-01-25 12:08:58 | 2022-01-25 12:09:31 | 2022-01-25 12:10:11 | 2022-01-25 12:10:53 | Packiyaraj | Replaced new bulb | [6 empty] | Light flickering-packiyaraj-low
FID6704 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1071 |  | 2022-01-25 09:29:04 | 2022-01-25 09:33:01 | 2022-01-25 09:33:23 | 2022-01-25 09:33:46 | 2022-01-25 09:34:08 | 2022-01-25 09:55:12 | FRC | Adjusted vav 1-2-7 damper position from 23.8% (auto) to 50% manual in bms system make it cool. Thermostat setting at 23c. | [6 empty] | Aircon too warm, make it cool-Su-low
FID6703 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1070 |  | 2022-01-25 09:28:21 | 2022-01-25 09:30:09 | 2022-01-25 09:30:33 | 2022-01-25 09:30:55 | 2022-01-25 09:32:18 | 2022-01-25 09:56:24 | FRC | Adjusted vav 1-2-8 damper position from 0% manual to auto (90%) in bms system make it cool. Thermostat setting at 15.1c. | [6 empty] | Aircon too warm, make it cool-Su-low
FID6701 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre Consult Rm 15 |  | 2022-01-25 09:26:20 | 2022-01-25 12:12:38 | 2022-01-25 12:15:21 | 2022-01-25 12:15:44 | 2022-01-25 12:15:52 | 2022-01-25 12:19:44 | Packiyaraj | Replaced new starter | [6 empty] | light flickering-packiyaraj-low
FID6700 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1070 |  | 2022-01-25 09:24:10 | 2022-01-31 11:37:05 | 2022-01-31 11:37:25 | 2022-01-31 11:37:50 | 2022-01-31 11:38:22 | 2022-01-31 11:38:56 | FRC | Adjusted the temperature setpoint and damper position for the room vav in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6699 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > 25 Tannery Lane > 7 > TL-7-27 Office |  | 2022-01-25 09:22:01 | 2022-01-31 11:27:46 | 2022-01-31 11:28:07 | 2022-01-31 11:32:47 | 2022-01-31 11:33:06 | 2022-01-31 11:33:55 | FRC | Replaced new light | [6 empty] | Light fused-ela-low
FID6698 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Affecting Public | RMG > RH > 2 > RM@RH Consult Rm 3 |  | 2022-01-25 09:20:19 | 2022-01-31 10:43:11 | 2022-01-31 11:18:05 | 2022-01-31 11:20:00 | 2022-01-31 11:22:16 | 2022-01-31 11:27:03 | FRC | Adjusted the room vav damper position in bms system to reduce the airflow | [6 empty] | Airflow too strong-Aru-low
FID6697 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 9 > Ward 921 |  | 2022-01-25 09:19:03 | 2022-01-27 12:21:55 | 2022-01-27 12:22:21 | 2022-01-27 12:23:48 | 2022-01-27 12:24:11 | 2022-01-27 12:24:46 | Rajendran Manikandan | Reset normal back | [6 empty] | Need to check the call bell-Mani-low
FID6685 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU |  | 2022-01-25 06:45:57 | 2022-01-31 10:40:37 | 2022-01-31 10:41:01 | 2022-01-31 10:41:25 | 2022-01-31 10:41:50 | 2022-01-31 10:42:30 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6684 | Electrical | Light Bulb | Flickering / Blown | WIthin Building | RMG > RH > 6 > Carpark |  | 2022-01-24 22:06:43 | 2022-01-24 22:14:01 | 2022-01-24 22:14:27 | 2022-01-24 22:14:49 | 2022-01-24 22:15:16 | 2022-01-24 22:15:59 | Rajendran Manikandan | Replaced new bulb | [6 empty] | light flickering-mani-low
FID6683 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Main Lobby |  | 2022-01-24 22:05:20 | 2022-01-24 22:16:31 | 2022-01-24 22:16:53 | 2022-01-24 22:17:18 | 2022-01-24 22:17:43 | 2022-01-24 22:18:31 | Rajendran Manikandan | Replaced new bulb | [6 empty] | light flickering-mani-low
FID6682 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1053 |  | 2022-01-24 21:57:11 | 2022-01-31 10:37:56 | 2022-01-31 10:38:20 | 2022-01-31 10:38:46 | 2022-01-31 10:39:12 | 2022-01-31 10:39:46 | FRC | Adjusted the aircon temperature setpoint in bms system make it warm | [6 empty] | Aircon make it warm-Aru-low
FID6677 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Rm 702 |  | 2022-01-24 20:17:21 | 2022-01-24 20:24:36 | 2022-01-24 20:25:13 | 2022-01-24 20:25:51 | 2022-01-24 20:26:24 | 2022-01-24 20:28:28 | Vadivelu Balasubramanian | adjusted the temperature in isolation room display setpoint 18to22 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6673 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 3 > Kitchen |  | 2022-01-24 16:56:25 | 2022-01-24 18:15:25 | 2022-01-24 18:15:59 | 2022-01-24 18:16:45 | 2022-01-24 18:17:20 | 2022-01-24 18:20:42 | Packiyaraj | replaced bulb | [6 empty] | Light fused-Packiyaraj-low
FID6671 | Mechanical | Autodoor | Other: auto door cannot close | Affecting Public | RMG > RSC > 9 > Fireman Lift Lobby |  | 2022-01-24 16:34:26 | 2022-01-31 10:35:39 | 2022-01-31 10:36:02 | 2022-01-31 10:36:25 | 2022-01-31 10:36:48 | 2022-01-31 10:37:19 | FRC | reset the auto door power back to normal | [6 empty] | Auto door cannot close-Packiyaraj-low
FID6670 | Office and Furniture | Safe Box | Cannot operate / defective | Localised to room | RMG > RH > 10 > Ward 1036 |  | 2022-01-24 16:31:44 | 2022-01-24 20:11:12 | 2022-01-24 20:13:00 | 2022-01-24 20:15:31 | 2022-01-24 20:19:19 | 2022-01-24 20:21:39 | Arasan Balasubramanian | reset the safebox back to normal | [6 empty] | Safe box not working-a.bala-low
FID6667 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RSC > 16 > Eye Centre |  | 2022-01-24 16:05:53 | 2022-01-24 16:06:26 | 2022-01-24 16:06:45 | 2022-01-24 16:07:25 | 2022-01-24 16:07:45 | 2022-01-25 09:58:27 | FRC | Adjusted vav 16-2-4 temperature setpoint from 24c to 22c and damper position from 20% manual to 60% manual in bms system make it cool | [6 empty] | Aircon make it cool-Su-low
FID6666 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Ward 996 - 999 (Serology Lab) |  | 2022-01-24 16:05:00 | 2022-01-26 12:21:54 | 2022-01-26 12:22:24 | 2022-01-26 12:22:45 | 2022-01-26 12:23:08 | 2022-01-26 12:39:05 | Hossain | onsite check & found room temperature was 26.1c' & found VAV actuator valve 40% was open. Unable to open 100% VAV valve. Redirect to engineers Gray.. to rectify this issue. | [6 empty] | Aircon warm-Hossain-low
FID6665 | Building | Water Dispenser | Other: Tap broken | Affecting Public | RMG > RH > 2 > Healthcheck |  | 2022-01-24 16:04:16 | 2022-01-26 12:39:58 | 2022-01-26 12:40:28 | 2022-01-26 12:40:48 | 2022-01-26 12:41:09 | 2022-01-26 12:42:23 | Hossain | Onsite check & rectified the water dispenser tap back to normal. | [6 empty] | Water dispenser hot water tap broken-Hossain-low
FID6663 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RSC > 11 > Radiology |  | 2022-01-24 15:57:02 | 2022-01-24 19:09:28 | 2022-01-24 19:09:58 | 2022-01-24 19:10:25 | 2022-01-24 19:10:49 | 2022-01-24 19:14:32 | Vadivelu Balasubramanian | door lock knop struck use w 40 spray back to normal | [6 empty] | Door cannot close properly-V.bala-low
FID6662 | Plumbing & Sanitary | Soap Dispenser | Other: Need to shift | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2022-01-24 15:55:47 | 2022-01-27 09:21:40 | 2022-01-27 09:21:58 | 2022-01-27 09:22:15 | 2022-01-27 09:22:32 | 2022-01-27 09:23:05 | liumingcai | move up | [6 empty] | Need to shift the tissue box 6" up-ming cai-low
FID6661 | Building | Filter | Other: Dirty | Affecting Public | RMG > RH > 7 > Operating Theatre 1 (Endoscopy) |  | 2022-01-24 15:52:55 | 2022-01-27 09:23:30 | 2022-01-27 09:23:49 | 2022-01-27 09:24:07 | 2022-01-27 09:24:25 | 2022-01-27 09:25:19 | liumingcai | replace new | [6 empty] | Need to replace filter-ming cai-low
FID6653 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 7 > ICU Rm 703 |  | 2022-01-24 14:49:07 | 2022-01-24 19:15:44 | 2022-01-24 19:16:26 | 2022-01-24 19:17:00 | 2022-01-24 19:17:28 | 2022-01-24 19:18:06 | Vadivelu Balasubramanian | replaced hose | [6 empty] | Bidet spray leaking-V.Bala-low
FID6651 | Office and Furniture | Telephone | Cannot operate / defective | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-24 14:28:09 | 2022-01-31 10:33:08 | 2022-01-31 10:33:30 | 2022-01-31 10:33:55 | 2022-01-31 10:34:18 | 2022-01-31 10:34:57 | FRC | IP telephone handset faulty, need to repair. Pending | [6 empty] | Telephone (ext 2092) sometimes cannot hear and voice very soft-A.Bala-low
FID6649 | Medical Equipment | Bedpan Macerator & Sanitizer | Leaking | Affecting Public | RMG > RH > 8 > Labour Ward Soil Utility Rm |  | 2022-01-24 14:14:50 | 2022-01-26 12:44:06 | 2022-01-26 12:45:24 | 2022-01-26 12:45:45 | 2022-01-26 12:46:35 | 2022-01-26 12:57:37 | Hossain | Onsite check & found water leaking from the bedpan sanitizer. Informed engineer Murogan he said that will inform to contractor & close the water supply valve. i closed the water supply valve & updated accordingly to user. | [6 empty] | Water leaking from the bedpan sanitizer-Hossain-low
FID6648 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > RCM Dispensary |  | 2022-01-24 14:13:43 | 2022-01-31 10:28:50 | 2022-01-31 10:29:25 | 2022-01-31 10:29:49 | 2022-01-31 10:30:14 | 2022-01-31 10:31:04 | FRC | Adjusted vav 5-1-16 temperature setpoint from 21c to 23c and damper from 100% manual to 70% manual in bms system make it slightly warm | [6 empty] | Aircon too cold, make it warm-Jailani-low
FID6647 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > RCM Counter |  | 2022-01-24 14:12:21 | 2022-01-31 10:16:43 | 2022-01-31 10:17:08 | 2022-01-31 10:17:47 | 2022-01-31 10:18:30 | 2022-01-31 10:27:23 | FRC | Checked with staff onsite., they informed no need to do any adjustment as the temperature is within the range. | [6 empty] | Aircon too cold, make it warm-Jailani-low
FID6646 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2022-01-24 13:46:52 | 2022-01-24 13:47:10 | 2022-01-24 13:47:27 | 2022-01-24 13:47:43 | 2022-01-24 13:47:59 | 2022-01-24 14:10:49 | FRC | adjusted VAV 2-3-6 damper position from auto (20%) to 60% manual in BMS system make it cool. thermostat setting is 22.4c | [6 empty] | Aircon make it cool-Su-low
FID6645 | Building | Door Closer | Unable to open or close properly | Localised to room | RMG > RH > 9 > Business Centre Office 2 |  | 2022-01-24 13:45:44 | 2022-01-24 19:19:57 | 2022-01-24 19:20:24 | 2022-01-24 19:20:49 | 2022-01-24 19:21:15 | 2022-01-24 19:22:15 | Vadivelu Balasubramanian | adjusted door closer screw normal | [6 empty] | Door close very loud-V.bala-low
FID6644 | Medical Equipment | Commode Chair | Other: cannot open | Affecting Public | RMG > RH > 10 > Nursing Stn B |  | 2022-01-24 13:44:35 | 2022-01-27 09:25:58 | 2022-01-27 09:26:17 | 2022-01-27 09:26:36 | 2022-01-27 09:26:58 | 2022-01-27 09:27:29 | liumingcai | open | [6 empty] | Wheelchair cannot open-Ming cai-low
FID6642 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: Noisy | Affecting Public | RMG > RH > 8 > Labour Ward Soil Utility Rm |  | 2022-01-24 13:27:39 | 2022-01-26 12:58:48 | 2022-01-26 12:59:48 | 2022-01-26 13:00:19 | 2022-01-26 13:00:41 | 2022-01-26 13:02:25 | Hossain | onsite check & got noisy utility room urinal flashing system. rectified the flashing system back to normal. | [6 empty] | Flush noisy-Hossain-low
FID6641 | Office and Furniture | Safe Box | Cannot operate / defective | Affecting Public | RMG > RH > 9 > Ward 980 - 986 |  | 2022-01-24 13:26:48 | 2022-01-24 13:58:17 | 2022-01-24 13:58:41 | 2022-01-24 13:58:59 | 2022-01-24 13:59:23 | 2022-01-24 14:00:04 | liumingcai | open | [6 empty] | Patient locker need to open-ming cai-low
FID6640 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RSC > B2 > Female Toilet |  | 2022-01-24 12:48:07 | 2022-01-24 13:55:39 | 2022-01-24 13:55:59 | 2022-01-24 13:56:21 | 2022-01-24 13:56:43 | 2022-01-24 13:57:49 | Chang Fook Keong Alan | Nothing cannot do stop very strong |  |  |  |  | 1 |  | Toilet bowl choke-Allan-low
FID6639 | Office and Furniture | Chair | Chipped / Cracked | More than 1 room | RMG > RH > 7 > OT |  | 2022-01-24 12:34:00 | 2022-01-27 20:33:51 | 2022-01-27 20:34:23 | 2022-01-31 10:04:38 | 2022-01-31 10:05:00 | 2022-01-31 10:10:03 | FRC | Repaired the chair |  |  |  |  | 1 |  | Chair faulty-Hossain-low
FID6638 | Electrical | Light Bulb | Other: satellite unable to focus | More than 1 room | RMG > RH > 7 > Operating Theatre 6 |  | 2022-01-24 12:22:56 | 2022-01-31 09:57:26 | 2022-01-31 09:59:01 | 2022-01-31 09:59:24 | 2022-01-31 09:59:47 | 2022-01-31 10:00:24 | FRC | Unable to adjust. Need to arrange vendor to check, pending |  |  |  |  | 1 |  | Operating light satellite unable to focus-Packiyaraj-low
FID6637 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 7 > OT |  | 2022-01-24 11:59:37 | 2022-01-24 19:23:27 | 2022-01-24 19:23:56 | 2022-01-24 19:24:22 | 2022-01-24 19:24:50 | 2022-01-24 19:28:41 | Vadivelu Balasubramanian | replaced big co2 cylinder 1 | [6 empty] | Need to replace 1 big CO2 cylinder-V.bala-medium
FID6636 | Building | Window | Other: Window not lock | Affecting Public | RMG > RH > 9 > Ward 954 (BMT) |  | 2022-01-24 11:58:48 | 2022-01-24 13:58:30 | 2022-01-24 13:58:49 | 2022-01-24 13:59:08 | 2022-01-24 13:59:26 | 2022-01-24 14:00:10 | Chang Fook Keong Alan | The window I have locked back | [6 empty] | Need to close window-Allan-low
FID6632 | Electrical | Socket | Unserviceable | Affecting Public | RMG > RH > 7 > Operating Theatre 11 |  | 2022-01-24 11:10:30 | 2022-01-24 19:31:39 | 2022-01-24 19:32:12 | 2022-01-24 19:32:55 | 2022-01-24 19:33:46 | 2022-01-24 19:35:21 | Vadivelu Balasubramanian | socket power no coming reset back normal | [6 empty] | AU pendant socket not working-V.Bala-low
FID6629 | Mechanical | Data Logger | Other: Data logger not recording | Affecting Public | RMG > RH > 2 > RM@RH Dispensary |  | 2022-01-24 10:32:17 | 2022-01-31 09:53:38 | 2022-01-31 09:54:10 | 2022-01-31 09:54:49 | 2022-01-31 09:55:15 | 2022-01-31 09:56:37 | FRC | reset the data logger settings | [6 empty] | Testo data logger not recording-Jailani-low
FID6627 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 7 > Operating Theatre 7 |  | 2022-01-24 10:11:28 | 2022-01-24 19:36:50 | 2022-01-24 19:37:32 | 2022-01-24 19:38:10 | 2022-01-24 19:38:42 | 2022-01-24 19:40:20 | Vadivelu Balasubramanian | medical air hose come out fixed back normal | [6 empty] | Medical air pendant show zero flow in pipeline-V.bala-medium
FID6626 | Plumbing & Sanitary | WC / Squatting Pedestal | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 7 > OT Male Channing Rm |  | 2022-01-24 10:08:35 | 2022-01-26 13:05:34 | 2022-01-26 13:06:46 | 2022-01-26 13:07:15 | 2022-01-26 13:07:36 | 2022-01-26 14:13:19 | Hossain | replaced the toilet seat cover as per request. | [6 empty] | Need to change toilet seat cover-Hossain-low
FID6625 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > ICU Rm 702 |  | 2022-01-24 10:07:43 | 2022-01-28 17:35:03 | 2022-01-28 17:53:54 | 2022-01-28 17:54:15 | 2022-01-28 17:54:38 | 2022-01-31 09:52:53 | FRC | Replaced new light | [6 empty] | Light fused-A.Bala-low
FID6623 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre Counter |  | 2022-01-24 10:06:43 | 2022-01-24 11:24:51 | 2022-01-24 11:25:22 | 2022-01-24 11:26:12 | 2022-01-24 11:26:56 | 2022-01-24 11:27:38 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6622 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Day Surgery |  | 2022-01-24 10:01:54 | 2022-01-26 13:08:50 | 2022-01-26 13:34:49 | 2022-01-26 13:35:20 | 2022-01-26 13:35:50 | 2022-01-26 13:36:31 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6621 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Operating Theatre 8 |  | 2022-01-24 10:01:04 | 2022-01-26 13:02:59 | 2022-01-26 13:03:48 | 2022-01-26 13:04:20 | 2022-01-26 13:04:48 | 2022-01-26 13:06:15 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6620 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Operating Theatre 7 |  | 2022-01-24 09:59:47 | 2022-01-26 10:23:25 | 2022-01-26 10:23:37 | 2022-01-26 10:23:55 | 2022-01-26 10:24:10 | 2022-01-26 10:24:49 | Packiyaraj | Replaced bulb | [6 empty] | Light flickering-packiyaraj-low
FID6609 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 11 > Level 11 |  | 2022-01-24 08:24:00 | 2022-01-26 10:25:40 | 2022-01-26 10:26:48 | 2022-01-26 10:27:14 | 2022-01-26 10:27:35 | 2022-01-26 10:28:18 | Packiyaraj | Replaced bulb | [6 empty] | Light fused-packiyaraj-low
FID6608 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-24 08:16:00 | 2022-01-28 17:13:40 | 2022-01-28 17:14:16 | 2022-01-28 17:32:56 | 2022-01-28 17:33:16 | 2022-01-28 17:34:07 | FRC | Adjusted the aircon temperature make it cool in bms system | [6 empty] | Aircon make it cool-aru-low
FID6606 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-24 07:34:33 | 2022-01-24 07:36:52 | 2022-01-24 07:37:26 | 2022-01-24 07:37:52 | 2022-01-24 07:38:19 | 2022-01-24 07:39:24 | Rajendran Manikandan | change full cylinder and normal back | [6 empty] | Nitrogen alarming change cylinder-mani-medium
FID6605 | Mechanical | Lift & Escalators | Tripped / Short-Circuit / Overloaded | Affecting Public | RMG > RSC > 1 > Lobby |  | 2022-01-24 07:24:48 | 2022-01-24 07:25:41 | 2022-01-24 07:26:07 | 2022-01-24 07:26:30 | 2022-01-24 07:26:57 | 2022-01-24 07:27:59 | Rajendran Manikandan | Reset normal back | [6 empty] | Escalator 07 not running-mani-low
FID6604 | Electrical | Lightning Protection System | Tripped / Short-Circuit / Overloaded | Localised to room | RMG > RH > 11 > Level 11 |  | 2022-01-24 04:25:37 | 2022-01-24 04:26:25 | 2022-01-24 04:26:45 | 2022-01-24 04:27:06 | 2022-01-24 04:27:29 | 2022-01-24 04:28:32 | Rajendran Manikandan | Reset normal back | [6 empty] | Power trip-mani-high
FID6599 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1048 |  | 2022-01-23 18:09:14 | 2022-01-23 18:16:25 | 2022-01-23 18:16:59 | 2022-01-23 18:17:27 | 2022-01-23 18:18:25 | 2022-01-23 18:19:49 | Arasan Balasubramanian | adjusted the temprature aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-A.Bala-low
FID6589 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1048 |  | 2022-01-23 12:08:46 | 2022-01-28 17:10:37 | 2022-01-28 17:11:00 | 2022-01-28 17:11:45 | 2022-01-28 17:12:07 | 2022-01-28 17:12:42 | FRC | Adjusted the room vav temperature setpoint in bms system make it warm |  |  |  |  | 1 |  | Aircon make it warm-Nazri-low
FID6587 | Medical Equipment | Medical Gas | Leaking | More than 1 room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-23 11:17:22 | 2022-01-24 19:43:22 | 2022-01-24 19:44:16 | 2022-01-24 19:44:56 | 2022-01-24 19:45:34 | 2022-01-24 19:47:51 | Vadivelu Balasubramanian | 02 no leaking medical air leaking hose come out fixed back normal |  |  |  |  | 1 |  | Oxygen pendant leaking-V.Bala-medium
FID6586 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1045 |  | 2022-01-23 10:54:00 | 2022-01-23 11:19:31 | 2022-01-23 11:20:28 | 2022-01-23 11:21:19 | 2022-01-23 11:22:21 | 2022-01-23 11:53:53 | Arasan Balasubramanian | adjusted temprature make it cold |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID6584 | Plumbing & Sanitary | Floor trap | Choked | More than 1 room | RMG > RSC > 1 > Bin Centre |  | 2022-01-23 10:43:22 | 2022-01-28 17:08:14 | 2022-01-28 17:08:34 | 2022-01-28 17:08:55 | 2022-01-28 17:09:17 | 2022-01-28 17:09:50 | FRC | Cleared the floor trap choke |  |  |  |  | 1 |  | Floor trap choke-nazri-low
FID6579 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-23 00:19:14 | 2022-01-23 00:19:50 | 2022-01-23 00:23:53 | 2022-01-23 00:24:26 | 2022-01-23 00:24:59 | 2022-01-23 00:26:37 | Sivalingam Ilayaraja | adjested the temprature from bms yhrn make it warm | [6 empty] | Aircon too cool, make it warm-ilayaraja-low
FID6561 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-22 19:46:33 | 2022-01-22 19:48:36 | 2022-01-22 19:48:56 | 2022-01-22 19:49:14 | 2022-01-22 19:49:34 | 2022-01-22 19:51:15 | FRC | adjusted temperature setpoint from 24cto26c and manual in BMS system make it warm | [6 empty] | Aircon make it warm-mani-low
FID6556 | Mechanical | Data Logger | Other: Not recording | Affecting Public | RMG > RH > 2 > RM@RH |  | 2022-01-22 12:09:14 | 2022-01-28 17:05:26 | 2022-01-28 17:06:03 | 2022-01-28 17:06:28 | 2022-01-28 17:06:48 | 2022-01-28 17:07:33 | FRC | Reset the data logger parameters | [6 empty] | Data logger not recording-Aru-low
FID6554 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-22 11:46:21 | 2022-01-24 14:02:22 | 2022-01-24 14:02:42 | 2022-01-24 14:03:06 | 2022-01-24 14:03:29 | 2022-01-24 14:04:13 | Chang Fook Keong Alan | Clear the choke | [6 empty] | Toilet floor trap choke-Allan-low
FID6553 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 6 |  | 2022-01-22 10:40:13 | 2022-01-22 10:40:34 | 2022-01-22 10:41:09 | 2022-01-22 10:41:29 | 2022-01-22 10:41:47 | 2022-01-22 10:42:42 | FRC | adjusted temperature setpoint from 22c to 26c and heater from 50% manual to 80% manual in BMS system make it warm | [6 empty] | Aircon make it warm-Su-low
FID6550 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 7 > Level 7 |  | 2022-01-22 10:08:27 | 2022-01-27 20:36:33 | 2022-01-27 20:37:07 | 2022-01-27 20:37:27 | 2022-01-27 20:37:41 | 2022-01-28 17:04:40 | FRC | Checked and rectified | [6 empty] | CO2 gas pressure dropped-Hossain-medium
FID6549 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Healthcheck Consult Rm 9 |  | 2022-01-22 10:04:26 | 2022-01-22 10:05:17 | 2022-01-22 10:05:45 | 2022-01-22 10:06:08 | 2022-01-22 10:06:31 | 2022-01-22 10:13:43 | FRC | Adjusted vav 1-1-7 temperature setpoint from 20c to 22c and damper position 100% manual to 60% manual in bms system make it warm | [6 empty] | Aircon make it warm-su-low
FID6547 | Plumbing & Sanitary | Hot Water System | No water | Affecting Public | RMG > RH > 8 > Ward 835 (Victoria Suite Guest Rm) |  | 2022-01-22 09:21:53 | 2022-01-22 09:25:10 | 2022-01-22 09:26:52 | 2022-01-22 09:32:34 | 2022-01-22 09:33:10 | 2022-01-22 09:34:07 | Muthu Shanmugavelu | Got hot water.need to wait for few seconds.Explained staff | [6 empty] | No hot water-Shanmu-low
FID6546 | Plumbing & Sanitary | Shower Fittings | Other: No hot water | Affecting Public | RMG > RH > 8 > Ward 833 (Victoria Suite) |  | 2022-01-22 09:21:12 | 2022-01-22 09:22:25 | 2022-01-22 09:23:22 | 2022-01-22 09:23:45 | 2022-01-22 09:24:07 | 2022-01-22 09:24:31 | FRC | All rooms got hot water.Explained staff need to wait for few seconds.. | [6 empty] | No hot water-Shanmu-low
FID6545 | Plumbing & Sanitary | Water Heater | No water | Localised to room | RMG > RH > 8 > Ward 836 |  | 2022-01-22 09:15:47 | 2022-01-22 09:16:09 | 2022-01-22 09:16:26 | 2022-01-22 09:16:43 | 2022-01-22 09:16:59 | 2022-01-22 09:18:37 | Muthu Shanmugavelu | All rooms got hot water.Explained staff need to wait for few seconds.. | [6 empty] | No hot water-Shanmu-low
FID6544 | Medical Equipment | Medical Gas | Leaking | Affecting Public | RMG > RH > 8 > Ward 865-866 |  | 2022-01-22 09:15:04 | 2022-01-22 09:34:54 | 2022-01-22 09:35:14 | 2022-01-22 09:35:33 | 2022-01-22 09:35:53 | 2022-01-22 09:37:15 | Muthu Shanmugavelu | Replaced orings and outlet at beds 865,866 | [6 empty] | Oxygen terminal leaking-Hossain-medium
FID6520 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 9 > Ward 922 |  | 2022-01-22 04:29:39 | 2022-01-22 04:31:15 | 2022-01-22 04:31:34 | 2022-01-22 04:31:57 | 2022-01-22 04:32:20 | 2022-01-22 04:33:40 | Muthu Sathasivam | Aircon adjusted on thermostat by sister working normal . patient sleeping so sister says don't want go in . | [6 empty] | Aircon make it warm-satha-low
FID6518 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-22 01:43:48 | 2022-01-22 01:48:14 | 2022-01-22 01:48:53 | 2022-01-22 01:49:25 | 2022-01-22 01:49:43 | 2022-01-22 01:50:37 | Muthu Sathasivam | adjusted the setpoint temperature from 22 to 24 in auto . | [6 empty] | Aircon make warm-satha-low
FID6517 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1050 |  | 2022-01-21 23:23:26 | 2022-01-21 23:26:04 | 2022-01-21 23:26:34 | 2022-01-21 23:27:08 | 2022-01-21 23:27:37 | 2022-01-21 23:29:01 | Muthu Sathasivam | system all working normal temperature under control user need to set temperature to 22 degree from 24 degree adjusted in bms | [6 empty] | Aircon make cool-satha-low
FID6515 | Medical Equipment | Fridges & Freezers | Alarm | Localised to room | RMG > RH > 2 > RM@RH Dispensary |  | 2022-01-21 22:34:00 | 2022-01-21 22:35:07 | 2022-01-21 22:35:30 | 2022-01-21 22:35:51 | 2022-01-21 22:36:30 | 2022-01-21 22:37:45 | Muthu Sathasivam | checked on site fridge working normal . tms sensor covered with medicine clear the medicine | [6 empty] | Fridge alarming in tms, ch 27-satha-low
FID6514 | Mechanical | Air Handling Unit | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 703 |  | 2022-01-21 22:31:28 | 2022-01-21 22:38:10 | 2022-01-21 22:38:38 | 2022-01-21 22:39:01 | 2022-01-21 22:39:36 | 2022-01-21 22:41:05 | Muthu Sathasivam | setpoint setted to 18 degree on digital meter and changed to 24 as per user request | [6 empty] | Aircon make it warm-satha-low
FID6508 | Office and Furniture | Safe Box | Cannot open / close | Affecting Public | RMG > RH > 10 > Ward 1042 |  | 2022-01-21 17:45:59 | 2022-01-21 22:49:24 | 2022-01-21 22:50:19 | 2022-01-21 22:50:41 | 2022-01-21 22:51:10 | 2022-01-21 22:52:37 | Rajendran Manikandan | Reset normal back | [6 empty] | Safe box faulty-mani-low
FID6507 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre |  | 2022-01-21 17:45:09 | 2022-01-21 22:53:16 | 2022-01-21 22:53:40 | 2022-01-21 22:54:06 | 2022-01-21 22:54:33 | 2022-01-21 22:55:22 | Rajendran Manikandan | Replaced new bulb | [6 empty] | light flickering-mani-low
FID6506 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 9 > Ward 921 |  | 2022-01-21 17:40:08 | 2022-01-26 10:29:23 | 2022-01-26 10:29:58 | 2022-01-26 10:30:23 | 2022-01-28 16:36:48 | 2022-02-07 14:56:59 | FRC | Faceplate faulty, unable to repair. Need to arrange contractor. Pending | [6 empty] | Call bell not working-Packiyaraj-low
FID6502 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > OT Dirty Corridor |  | 2022-01-21 15:40:29 | 2022-01-21 18:44:11 | 2022-01-21 18:44:29 | 2022-01-21 18:45:05 | 2022-01-21 18:45:30 | 2022-01-21 18:46:03 | Packiyaraj | Replaced new bulb | [6 empty] | Light flickering-packiyaraj-low
FID6501 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > OT Dirty Corridor |  | 2022-01-21 15:39:21 | 2022-01-28 16:34:41 | 2022-01-28 16:35:02 | 2022-01-28 16:35:23 | 2022-01-28 16:35:44 | 2022-01-28 16:36:07 | FRC | Replaced new light | [6 empty] | Light flickering-packiyaraj-low
FID6492 | Office and Furniture | Printer | Cannot operate / defective | Affecting Public | RMG > RH > 9 > Nursing Stn B |  | 2022-01-21 13:31:02 | 2022-01-21 13:59:54 | 2022-01-21 14:00:22 | 2022-01-21 14:00:47 | 2022-01-21 14:01:09 | 2022-01-21 14:03:09 | Rajendran Manikandan | normal back | [6 empty] | Printer jammed-mani-low
FID6491 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Affecting Public | RMG > RH > 9 > Ward 905 |  | 2022-01-21 13:30:11 | 2022-01-21 14:04:07 | 2022-01-21 14:04:27 | 2022-01-21 14:04:45 | 2022-01-21 14:05:04 | 2022-01-21 14:05:47 | Chang Fook Keong Alan | I have change a new set | [6 empty] | Bidet spray leaking-Allan-low
FID6489 | Mechanical | AHU / FCU / CU | System Shows fault / Error code | Localised to room | RMG > RH > 9 > Ward 954 (BMT) |  | 2022-01-21 12:40:34 | 2022-01-28 16:31:47 | 2022-01-28 16:32:09 | 2022-01-28 16:32:32 | 2022-01-28 16:32:53 | 2022-01-28 16:33:45 | FRC | Upon reaching on site, the room pressure display panel is working normal, no more alarm. Informed to staff to monitor. | [6 empty] | Room temperature display alarming-Jailani-low
FID6488 | Building | Door Lock | Noisy | Localised to room | RMG > RH > 2 > Healthcheck Treatment Rm 8 |  | 2022-01-21 12:37:16 | 2022-01-21 14:06:31 | 2022-01-21 14:06:51 | 2022-01-21 14:07:10 | 2022-01-21 14:07:29 | 2022-01-21 14:08:14 | Chang Fook Keong Alan | Have inform to the usual the door cannot repair | [6 empty] | Door closer faulty-Allan-low
FID6487 | Mechanical | Pneumatic Tube | Missing | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-21 11:51:45 | 2022-01-21 12:21:03 | 2022-01-21 12:21:24 | 2022-01-21 12:21:44 | 2022-01-21 12:22:13 | 2022-01-21 12:23:18 | Muthu Shanmugavelu | found missing tube at Ward 13 and sent back to A&E | [6 empty] | Pneumatic tube missing-Shanmu-low
FID6486 | Building | Window | Unable to open or close properly | Affecting Public | RMG > RH > 9 > Ward 901 |  | 2022-01-21 11:37:13 | 2022-01-27 09:29:27 | 2022-01-27 09:29:45 | 2022-01-27 09:30:02 | 2022-01-27 09:30:19 | 2022-01-27 09:30:44 | liumingcai | close | [6 empty] | Window cannot close-ming cai-low
FID6484 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: Flush button stuck | Affecting Public | RMG > RSC > 16 > Male Toilet |  | 2022-01-21 10:57:23 | 2022-01-21 14:09:00 | 2022-01-21 14:09:21 | 2022-01-21 14:09:40 | 2022-01-21 14:10:14 | 2022-01-21 14:10:59 | Chang Fook Keong Alan | I have change the news set | [6 empty] | Toilet flush button stuck-Allan-low
FID6481 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RH > 2 > Healthcheck Treatment Rm 8 |  | 2022-01-21 10:07:19 | 2022-01-28 16:24:11 | 2022-01-28 16:24:35 | 2022-01-28 16:24:56 | 2022-01-28 16:26:04 | 2022-01-28 16:26:36 | FRC | Need to arrange contractor to repair the door, pending | [6 empty] | Door faulty-Hossain-low
FID6480 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Affecting Public | RMG > RH > 10 > Ward 1011 |  | 2022-01-21 10:05:39 | 2022-01-28 16:17:13 | 2022-01-28 16:17:33 | 2022-01-28 16:17:54 | 2022-01-28 16:18:16 | 2022-01-28 16:19:07 | FRC | Checked and found the fridge thermostat setting was too high. Adjusted lower to make the fridge cooler. | [6 empty] | Fridge not cold-Jailani-low
FID6477 | Medical Equipment | Patient Bed | Other: Cannot operate | Affecting Public | RMG > RH > 10 > Ward 1011 |  | 2022-01-21 09:41:08 | 2022-01-21 14:11:37 | 2022-01-21 14:11:56 | 2022-01-21 14:12:18 | 2022-01-21 14:12:37 | 2022-01-21 14:13:34 | Chang Fook Keong Alan | We have reset now can Operate | [6 empty] | Patient bed cannot adjust-Allan-low
FID6476 | Office and Furniture | Telephone | Cannot operate / defective | Affecting Public | RMG > RH > 10 > Ward 1023 |  | 2022-01-21 09:40:11 | 2022-01-21 10:04:21 | 2022-01-21 10:04:42 | 2022-01-21 10:04:51 | 2022-01-21 10:05:19 | 2022-01-21 10:06:13 | Packiyaraj | fix back telephone | [6 empty] | Need to fix the telephone-packiyaraj-low
FID6475 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RH > 12 > Women Centre Counter |  | 2022-01-21 09:37:36 | 2022-01-21 10:07:21 | 2022-01-21 10:07:50 | 2022-01-21 10:08:18 | 2022-01-21 10:09:02 | 2022-01-21 10:10:37 | Rajendran Manikandan | Replaced new TV remote better | [6 empty] | TV cannot on-mani-low
FID6472 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RSC > 10 > Handicap Toilet |  | 2022-01-21 08:24:53 | 2022-01-21 08:43:29 | 2022-01-21 08:44:23 | 2022-01-21 09:16:39 | 2022-01-21 09:17:17 | 2022-01-21 09:18:18 | Packiyaraj | Replaced transformer |  |  |  |  | 1 |  | Light flickering-packiyaraj-low
FID6470 | Office and Furniture | Wall Clock | Other: battery change | More than 1 room | RMG > RH > 8 > Ward 839 |  | 2022-01-21 08:22:12 | 2022-01-21 08:35:11 | 2022-01-21 08:35:39 | 2022-01-21 08:36:04 | 2022-01-21 08:36:31 | 2022-01-21 08:37:25 | Vadivelu Balasubramanian | replaced battery |  |  |  |  | 1 |  | Wall clock battery need to change-V.Bala-low
FID6467 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 12 > Women Centre Counter |  | 2022-01-21 07:34:08 | 2022-01-21 07:35:04 | 2022-01-21 08:48:42 | 2022-01-21 09:24:16 | 2022-01-21 09:27:38 | 2022-01-21 09:29:25 | Arasan Balasubramanian | replaced new light bulb |  |  |  |  | 1 |  | Light flickering-A.Bala-low
FID6463 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1050 |  | 2022-01-21 04:45:12 | 2022-01-21 07:21:01 | 2022-01-21 07:21:36 | 2022-01-21 07:22:07 | 2022-01-21 07:22:39 | 2022-01-21 07:24:56 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6461 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1050 |  | 2022-01-21 00:59:45 | 2022-01-21 07:25:57 | 2022-01-21 07:26:38 | 2022-01-21 07:27:09 | 2022-01-21 07:27:38 | 2022-01-21 07:28:47 | Vadivelu Balasubramanian | adjusted the temperature in bms vav control setpoint 24to22 make it cool |  |  |  |  | 1 |  | Aircon make cool-V.Bala-low
FID6460 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-21 00:41:33 | 2022-01-21 07:30:11 | 2022-01-21 07:30:56 | 2022-01-21 07:31:26 | 2022-01-21 07:31:54 | 2022-01-21 07:34:22 | Vadivelu Balasubramanian | adjusted temperature in bms vav control damper position make it warm in 90to20 |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6457 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1029 |  | 2022-01-20 18:49:07 | 2022-01-20 18:49:32 | 2022-01-20 18:49:58 | 2022-01-20 18:50:18 | 2022-01-20 18:51:35 | 2022-01-20 18:52:49 | Muthu Sathasivam | damper position set 80% manually change the setting to auto | [6 empty] | Aircon very cool, make it warm-satha-low
FID6456 | Plumbing & Sanitary | Floor trap | Leaking | Localised to room | RMG > RH > 12 > Housekeeping Office |  | 2022-01-20 18:47:31 | 2022-01-28 15:47:07 | 2022-01-28 16:04:10 | 2022-01-28 16:07:50 | 2022-01-28 16:14:09 | 2022-02-07 14:55:23 | FRC | Checked onsite, no water dripping from ceiling. However, ceiling board badly damaged due to previous leak. Need to replace new ceiling board. Pending | [6 empty] | Water dripping from celling-nazri-low
FID6455 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 8 > Labour Ward |  | 2022-01-20 18:44:33 | 2022-01-20 18:51:08 | 2022-01-20 19:01:31 | 2022-01-20 19:05:48 | 2022-01-20 19:06:25 | 2022-01-20 19:14:23 | Muthu Sathasivam | cooling valve jammed and reset back to normal | [6 empty] | Aircon very cool, make it warm-satha-low
FID6454 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Localised to room | RMG > RSC > B2 > Female Toilet |  | 2022-01-20 18:42:57 | 2022-01-21 09:57:26 | 2022-01-21 09:57:47 | 2022-01-21 09:58:06 | 2022-01-21 09:58:26 | 2022-01-21 09:59:22 | Chang Fook Keong Alan | I have clear the Chok | [6 empty] | Toilet bowl choke-allan-low
FID6453 | Office and Furniture | Cabinet | Other: lock spoiled | Localised to room | RMG > RH > 11 > Room 1126 (HR) |  | 2022-01-20 18:40:34 | 2022-01-28 15:42:58 | 2022-01-28 15:43:23 | 2022-01-28 15:44:12 | 2022-01-28 15:44:31 | 2022-01-28 15:44:59 | FRC | Repaired the pedestal | [6 empty] | Pedastal lock part come out-hossain-low
FID6448 | Plumbing & Sanitary | Floor trap | Leaking | Affecting Public | RMG > RSC > B2 > Female Toilet |  | 2022-01-20 17:13:37 | 2022-01-21 10:00:24 | 2022-01-21 10:00:47 | 2022-01-21 10:01:07 | 2022-01-21 10:01:28 | 2022-01-21 10:02:26 | Chang Fook Keong Alan | I have cleared the Chok | [6 empty] | Water leaking on the floor-Allan-low
FID6447 | Building | Door Closer | Noisy | Affecting Public | RMG > RSC > 8 > Handicap Toilet |  | 2022-01-20 17:12:32 | 2022-01-28 15:38:53 | 2022-01-28 15:39:23 | 2022-01-28 15:40:13 | 2022-01-28 15:41:17 | 2022-01-28 15:42:02 | FRC | Door bottom part broken. Need to arrange contractor. Pending | [6 empty] | Door got noise-Ming cai-low
FID6443 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Nursing Stn B |  | 2022-01-20 16:24:07 | 2022-01-28 15:34:58 | 2022-01-28 15:35:40 | 2022-01-28 15:36:20 | 2022-01-28 15:36:42 | 2022-01-28 15:37:44 | FRC | Checked onsite the temperature is at 22.4c. Informed to sister, they informed that it is ok. Hence, no adjustments made. | [6 empty] | Aircon make it cool-Jailani-low
FID6442 | Office and Furniture | Cabinet | Other: Parts come out | Affecting Public | RMG > RH > 11 > Room 1126 (HR) |  | 2022-01-20 16:23:23 | 2022-01-28 15:21:39 | 2022-01-28 15:22:01 | 2022-01-28 15:22:26 | 2022-01-28 15:22:48 | 2022-01-28 15:23:19 | FRC | Fixed the pedestal | [6 empty] | Pedestal parts come out-nazri-low
FID6439 | Medical Equipment | Medical Gas | Leaking | Localised to room | RMG > RH > 7M > Level 7M |  | 2022-01-20 15:15:49 | 2022-01-20 15:16:10 | 2022-01-20 15:16:27 | 2022-01-20 15:16:47 | 2022-01-20 15:17:06 | 2022-01-20 15:17:54 | Muthu Shanmugavelu | Replaced new adapter and no leakage found. | [6 empty] | Medical air tube leaking at 7m-Shanmu-high
FID6438 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-20 15:09:19 | 2022-01-20 15:09:43 | 2022-01-20 15:10:01 | 2022-01-20 15:10:21 | 2022-01-20 15:10:40 | 2022-01-20 15:13:18 | Muthu Shanmugavelu | change full cylinder and back to normal | [6 empty] | Nitrogen alarming change cylinder- Shanmu-medium
FID6435 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Ward 903 |  | 2022-01-20 14:45:46 | 2022-01-28 15:08:31 | 2022-01-28 15:08:52 | 2022-01-28 15:09:15 | 2022-01-28 15:09:35 | 2022-01-28 15:10:30 | FRC | Adjusted the thermostat setting from 21c to 23c on site make it warm | [6 empty] | Aircon too cold, make it warm-Jailani-low
FID6434 | Building | Door Closer | Leaking | Affecting Public | RMG > RSC > 12 > Rehab Toilet |  | 2022-01-20 14:44:28 | 2022-01-28 15:07:14 | 2022-02-07 14:52:43 | 2022-02-07 14:53:03 | 2022-02-07 14:53:43 | 2022-02-07 14:54:13 | FRC | Checked and rectified | [6 empty] | Water come out from the gap underneath the door when patient use the toilet-Ilayaraja-low
FID6430 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Localised to room | RMG > RSC > 1 > Male Toilet |  | 2022-01-20 12:20:10 | 2022-01-28 14:52:17 | 2022-01-28 14:56:31 | 2022-01-28 14:59:52 | 2022-01-28 15:00:26 | 2022-01-28 15:00:54 | FRC | Cleared the choke | [6 empty] | Toilet bowl choke-Hossain-low
FID6428 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-20 11:46:46 | 2022-01-28 14:49:30 | 2022-01-28 14:49:50 | 2022-01-28 14:50:16 | 2022-01-28 14:51:03 | 2022-01-28 14:51:33 | FRC | Replaced new oxygen cylinder | [6 empty] | Need to replace 1 small portable oxygen cylinder-Hossain-medium
FID6424 | Plumbing & Sanitary | Basin / sink | Other: Water flow very slow | Affecting Public | RMG > RSC > 22 > Handicap Toilet |  | 2022-01-20 11:00:56 | 2022-01-20 11:33:40 | 2022-01-20 11:33:59 | 2022-01-20 11:34:19 | 2022-01-20 11:34:45 | 2022-01-20 11:35:14 | liumingcai | clear up | [6 empty] | Basin water flow very slow-ming cai-low
FID6423 | Building | Floor | Other: Carpet come out | Affecting Public | RMG > RH > 1 > A&E Main Counter |  | 2022-01-20 10:59:05 | 2022-01-28 14:43:02 | 2022-01-28 14:46:18 | 2022-01-28 14:46:52 | 2022-01-28 14:47:13 | 2022-01-28 14:47:41 | FRC | Glue back the carpet | [6 empty] | Carpet come out-Hossain-low
FID6417 | Plumbing & Sanitary | Shower Fittings | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 9 > Ward 901 |  | 2022-01-20 10:24:24 | 2022-01-20 10:27:28 | 2022-01-20 10:28:33 | 2022-01-20 10:29:51 | 2022-01-20 10:30:44 | 2022-01-20 10:58:54 | Sivalingam Ilayaraja | replaced the new showerhead | [6 empty] | Shower head dropped-ilayaraja-low
FID6414 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Histo Data Rm |  | 2022-01-20 10:05:23 | 2022-01-28 14:32:20 | 2022-01-28 14:32:39 | 2022-01-28 14:32:58 | 2022-01-28 14:33:19 | 2022-01-28 14:37:32 | FRC | Replaced new light | [6 empty] | Light bulb flickering-nazri-low
FID6413 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RH > 2 > RJC Dispensary |  | 2022-01-20 10:04:18 | 2022-01-20 10:24:14 | 2022-01-20 10:34:01 | 2022-01-28 14:30:12 | 2022-01-28 14:31:06 | 2022-01-28 14:31:38 | FRC | Need to arrange contractor to do. Pending | [6 empty] | Door unable to open and close properly-ilayaraja-low
FID6406 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Ward 965 - 966 |  | 2022-01-20 08:08:11 | 2022-01-20 08:28:16 | 2022-01-20 08:28:52 | 2022-01-20 08:30:28 | 2022-01-20 08:44:23 | 2022-01-20 08:45:40 | Arasan Balasubramanian | replaced new light bulb |  |  |  |  | 1 |  | Light fused-a.bala-low
FID6403 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Rm 702 |  | 2022-01-20 04:05:55 | 2022-01-20 04:26:42 | 2022-01-20 04:27:08 | 2022-01-20 04:27:28 | 2022-01-20 04:27:51 | 2022-01-20 04:32:14 | Vadivelu Balasubramanian | adjusted the temperature in isolation room display setpoint 28to22 reduce make it cool |  |  |  |  | 1 |  | Aircon make it cold-v.bala-low
FID6402 | Electrical | Light Bulb | Other: light cannot off | More than 1 room | RMG > RH > 10 > Ward 1045 |  | 2022-01-20 03:49:02 | 2022-01-20 03:55:40 | 2022-01-20 03:56:12 | 2022-01-20 03:56:55 | 2022-01-20 03:57:48 | 2022-01-20 04:04:17 | Arasan Balasubramanian | temporary remove wire |  |  |  |  | 1 |  | Bed head light cannot off-a.bala-low
FID6401 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Level 13 |  | 2022-01-20 00:42:32 | 2022-01-20 01:01:27 | 2022-01-20 01:02:05 | 2022-01-20 01:02:44 | 2022-01-20 01:03:09 | 2022-01-20 01:07:09 | Vadivelu Balasubramanian | adjusted temperature in bms ahu 13-1 setpoint 16to17 ingress make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6400 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Counter A |  | 2022-01-19 23:16:33 | 2022-01-19 23:35:55 | 2022-01-19 23:36:30 | 2022-01-19 23:36:53 | 2022-01-19 23:37:03 | 2022-01-19 23:40:19 | Vadivelu Balasubramanian | adjusted temperature in bms ahu 7-1 setpoint 16to17 ingress make it warm |  |  |  |  | 1 |  | Aircon make it warm-v.bala-low
FID6396 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RH > 2 > Dental Surgery 9 |  | 2022-01-19 18:06:58 | 2022-01-19 18:21:12 | 2022-01-19 18:21:34 | 2022-01-19 18:22:05 | 2022-01-19 18:23:02 | 2022-01-19 18:23:50 | liumingcai | clear up | [6 empty] | Water leaking from the floor trap-ming cai-low
FID6395 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 2 > Dental Surgery 13 |  | 2022-01-19 18:06:16 | 2022-01-28 14:26:18 | 2022-01-28 14:26:38 | 2022-01-28 14:26:59 | 2022-01-28 14:27:20 | 2022-01-28 14:27:49 | FRC | Replaced new light | [6 empty] | Light not working-Hossain-low
FID6390 | Building | Door Knob / Handle | Misaligned / dangling | Affecting Public | RMG > RH > 11 > Room 1112 (Medisave off) |  | 2022-01-19 16:29:32 | 2022-01-19 16:47:28 | 2022-01-19 16:55:52 | 2022-01-19 16:56:41 | 2022-01-19 16:57:23 | 2022-01-19 16:59:14 | Sivalingam Ilayaraja | applied the wd40 spray then normal back | [6 empty] | Door knob too tight, need to adjust-ilayaraja-low
FID6389 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 8 > Ward 849 |  | 2022-01-19 15:58:28 | 2022-01-20 09:22:40 | 2022-01-20 09:23:08 | 2022-01-20 09:23:37 | 2022-01-20 09:23:57 | 2022-01-20 09:24:31 | FRC | replace new bulb | [6 empty] | Toilet mirror light fused-Packiyaraj-low
FID6388 | Building | Ceiling | Leaking | Affecting Public | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-19 15:38:23 | 2022-01-19 18:24:36 | 2022-01-19 23:20:30 | 2022-01-19 23:21:04 | 2022-01-19 23:55:01 | 2022-01-19 23:55:54 | liumingcai | stop the water | [6 empty] | Water leaking from ceiling-Ming Cai-low
FID6387 | Plumbing & Sanitary | Soap Dispenser | Damaged / Loose / Cracked | Affecting Public | RMG > RSC > 8 > Children Centre Dispensary |  | 2022-01-19 15:35:56 | 2022-01-19 15:36:27 | 2022-01-19 23:56:34 | 2022-01-19 23:56:52 | 2022-01-19 23:57:11 | 2022-01-19 23:57:57 | liumingcai | fix back | [6 empty] | Soap dispenser dropped-Ming Cai-low
FID6386 | Mechanical | Lift & Escalators (Schindler) | Other: Lift jerk | Affecting Public | RMG > RH > 11 > Level 11 |  | 2022-01-19 15:34:57 | 2022-01-28 14:22:12 | 2022-01-28 14:22:45 | 2022-01-28 14:23:11 | 2022-01-28 14:23:38 | 2022-01-28 14:24:27 | FRC | Informed to schindler to check. Rectified | [6 empty] | Visitor Lift 4 jerked when reach level 11 and door did not open-FRC-low
FID6385 | Mechanical | BMS / BAS | Other: Alarm | Affecting Public | RMG > RH > 9 > Ward 954 (BMT) |  | 2022-01-19 15:19:33 | 2022-01-28 14:05:16 | 2022-01-28 14:05:36 | 2022-01-28 14:06:36 | 2022-01-28 14:07:05 | 2022-01-28 14:07:53 | FRC | Upon reaching onsite, the room pressure was normal. Informed to the staff and monitor. | [6 empty] | Isolation room pressure display panel alarming-Azni-low
FID6383 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-19 14:45:19 | 2022-01-19 14:45:38 | 2022-01-19 14:45:55 | 2022-01-19 14:46:14 | 2022-01-19 14:46:32 | 2022-01-19 14:47:20 | Muthu Shanmugavelu | Replaced N2,allenox and N20 cylinders at standby dutybanks | [6 empty] | Replacing the empty cylinders in duty bank standby-Shanmu-medium
FID6379 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-19 13:12:55 | 2022-01-20 10:38:09 | 2022-01-20 10:38:35 | 2022-01-20 10:39:03 | 2022-01-20 10:39:40 | 2022-01-20 10:40:36 | Packiyaraj | Replaced new bulb | [6 empty] | Head light not working-packiyaraj-low
FID6378 | Plumbing & Sanitary | Flush Button | No water | Localised to room | RMG > 25 Tannery Lane > 6 > Female Toilet |  | 2022-01-19 13:04:17 | 2022-01-28 14:01:02 | 2022-01-28 14:02:34 | 2022-01-28 14:03:03 | 2022-01-28 14:03:39 | 2022-01-28 14:04:05 | FRC | Replaced new flushing system button | [6 empty] | Toilet bowl flush not working-Ela-low
FID6377 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RH > 11 > Room 1107 (QM) |  | 2022-01-19 12:48:39 | 2022-01-19 13:35:19 | 2022-01-19 13:36:55 | 2022-01-19 13:38:37 | 2022-01-19 13:42:13 | 2022-01-19 13:44:21 | Sivalingam Ilayaraja | replaced the bidet spray. | [6 empty] | Bidet spray leaking-ilayaraja-low
FID6376 | Mechanical | Air Handling Unit | Too hot / Too cold | Localised to room | RMG > RH > 7 > Angio Suite |  | 2022-01-19 12:24:42 | 2022-01-19 12:25:56 | 2022-01-19 12:34:40 | 2022-01-19 12:34:56 | 2022-01-19 12:35:32 | 2022-01-19 12:36:50 | Muthu Sathasivam | adjusted the setpoint temperature in bms from 12 degree to 14 degree | [6 empty] | Need to adjust the aircon temperature to 19c-satha-low
FID6375 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1028 |  | 2022-01-19 11:55:22 | 2022-01-19 12:01:25 | 2022-01-19 12:02:55 | 2022-01-19 12:03:19 | 2022-01-19 12:03:59 | 2022-01-19 13:25:14 | FRC | Adjusted VAV 2-3-3 damper position from auto (84.5%) to 100% manual in bms system make it cool. | [6 empty] | Aircon make it cool-su-low
FID6366 | Office and Furniture | Cabinet | Cannot open / close | Affecting Public | RMG > RH > 1 > Unit #01-11 Retail Phamacy |  | 2022-01-19 10:20:48 | 2022-01-19 11:20:10 | 2022-01-19 11:20:40 | 2022-01-19 11:21:02 | 2022-01-19 11:21:15 | 2022-01-19 11:23:15 | Hossain | onsite check & found cabinet hinge came off. Fixed properly the cabinet hinge back to normal. | [6 empty] | Cabinet door loose-Hossain-low
FID6365 | Building | Floor | Chipped / Cracked | Affecting Public | RMG > RH > 13 > Level 13 |  | 2022-01-19 09:54:47 | 2022-01-19 11:12:34 | 2022-01-19 11:12:52 | 2022-01-19 11:13:10 | 2022-01-19 11:13:30 | 2022-01-19 11:14:52 | Chang Fook Keong Alan | I have Fix back the crack | [6 empty] | Floor vinyl come out-Allan-low
FID6363 | Plumbing & Sanitary | Floor trap | Leaking | Affecting Public | RMG > RH > 10 > Stn C Utility Rm |  | 2022-01-19 09:44:33 | 2022-01-28 13:55:13 | 2022-01-28 13:55:34 | 2022-01-28 13:58:52 | 2022-01-28 13:59:14 | 2022-01-28 14:00:18 | FRC | Checked and rectified | [6 empty] | Water leaking, need to check-Aru-low
FID6362 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Affecting Public | RMG > RH > 8 > Ward 816 |  | 2022-01-19 09:42:27 | 2022-01-28 13:52:46 | 2022-01-28 13:53:18 | 2022-01-28 13:53:38 | 2022-01-28 13:53:59 | 2022-01-28 13:54:30 | FRC | Adjusted the fridge temperature setting make it cool | [6 empty] | Fridge not cold-Aru-low
FID6360 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Healthcheck Consult Rm 9 |  | 2022-01-19 09:37:56 | 2022-01-19 09:39:08 | 2022-01-19 09:39:27 | 2022-01-19 09:39:46 | 2022-01-19 09:40:06 | 2022-01-19 09:51:20 | FRC | Adjusted VAV 1-1-7 temperature setpoint from 22c to 20c and damper position from auto (90%) to 100% manual in bms system make it cool | [6 empty] | Aircon make it cool-su-low
FID6359 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Histo Data Rm |  | 2022-01-19 09:37:13 | 2022-01-19 12:27:26 | 2022-01-19 12:27:54 | 2022-01-19 12:28:22 | 2022-01-19 12:30:12 | 2022-01-19 12:31:40 | Muthu Sathasivam | user request close the diffuser | [6 empty] | Aircon too cold, make it warm-satha-low
FID6358 | Plumbing & Sanitary | WC / Squatting Pedestal | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 13 > Male Toilet (Waiting Area) |  | 2022-01-19 09:36:16 | 2022-01-19 11:24:20 | 2022-01-19 11:24:40 | 2022-01-19 11:24:47 | 2022-01-19 11:25:35 | 2022-01-19 11:29:08 | Hossain | onsite check & found wc seat cover was loose & unable to tighten due to seat cover hinge spoiled. replaced the toilet seat cover back to normal. | [6 empty] | Toilet seat cover loose-Hossain-low
FID6351 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 917 |  | 2022-01-19 08:04:04 | 2022-01-19 08:22:22 | 2022-01-19 08:22:53 | 2022-01-19 08:23:21 | 2022-01-19 08:23:46 | 2022-01-19 08:24:25 | Rajendran Manikandan | Reset normal back | [6 empty] | Call bell faulty-mani-low
FID6350 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Level 13 |  | 2022-01-19 07:59:49 | 2022-01-28 13:49:43 | 2022-01-28 13:50:03 | 2022-01-28 13:50:27 | 2022-01-28 13:50:50 | 2022-01-28 13:51:32 | FRC | Adjusted the temperature setpoint in bms system make it warm | [6 empty] | Whole area aircon very cool, need to make it warm-aru-low
FID6349 | Electrical | Socket | Other: no working | More than 1 room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-19 07:56:12 | 2022-01-26 13:42:08 | 2022-01-26 13:46:26 | 2022-01-26 13:47:47 | 2022-01-26 13:48:18 | 2022-01-26 13:49:37 | Packiyaraj | Reset RCCB back to normal | [6 empty] | Bed can't move-aru-low
FID6305 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RH > 9 > Ward 973 - 975 |  | 2022-01-18 17:28:38 | 2022-01-19 11:16:20 | 2022-01-19 11:16:39 | 2022-01-19 11:16:57 | 2022-01-19 11:17:22 | 2022-01-19 11:27:09 | Chang Fook Keong Alan | The TV has Spoil I have inform the user | [6 empty] | TV faulty-Allan-low
FID6304 | Medical Equipment | Patient Bed | Other: Need to shift | Affecting Public | RMG > RH > 12 > REMC RM 8 |  | 2022-01-18 17:27:52 | 2022-01-19 11:12:52 | 2022-01-19 11:26:43 | 2022-01-19 11:27:03 | 2022-01-19 11:27:36 | 2022-01-19 11:28:22 | liumingcai | shift the bed | [6 empty] | Need to shift the bed slightly-Nazri, ming cai-low
FID6300 | Medical Equipment | Patient Bed | Other: Bed cannot lock | Affecting Public | RMG > RSC > 9 > Internal Med Procedure Rm |  | 2022-01-18 15:44:27 | 2022-01-19 11:16:22 | 2022-01-19 11:16:40 | 2022-01-19 11:16:58 | 2022-01-19 11:17:16 | 2022-01-19 11:17:48 | liumingcai | repair | [6 empty] | Geriatric bed cannot lock-Ming cai-low
FID6299 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-18 15:43:27 | 2022-01-18 15:45:46 | 2022-01-18 15:46:06 | 2022-01-18 15:46:27 | 2022-01-18 15:46:57 | 2022-01-28 13:48:35 | FRC | Adjusted the temperature setpoint to 26c and heater from 0% manual to 60% manual in bms system make it warm | [6 empty] | Aircon too cold, make it warm-Su-low
FID6296 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: Toilet seat cover loosen | Affecting Public | RMG > RH > 2 > RM@RH |  | 2022-01-18 15:12:00 | 2022-01-19 11:29:27 | 2022-01-19 11:30:34 | 2022-01-19 11:31:08 | 2022-01-19 11:31:43 | 2022-01-19 11:32:11 | liumingcai | repair | [6 empty] | Toilet seat cover loosen-Nazri-low
FID6295 | Medical Equipment | Patient Bed | Other: Bed not working | Affecting Public | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-18 15:10:22 | 2022-01-19 11:04:55 | 2022-01-19 11:05:14 | 2022-01-19 11:08:12 | 2022-01-19 11:08:30 | 2022-01-19 11:09:08 | liumingcai | on the power | [6 empty] | Bed not working-Ming Cai-low
FID6294 | Plumbing & Sanitary | Bidet spray / Hose | Water flowing non-stop | Affecting Public | RMG > RH > 10 > Ward 1050 |  | 2022-01-18 14:20:10 | 2022-01-18 14:50:42 | 2022-01-18 14:51:37 | 2022-01-18 14:52:22 | 2022-01-18 14:53:05 | 2022-01-18 14:54:32 | Sivalingam Ilayaraja | replaced the new bidet spray. | [6 empty] | Bidet spray water non-stop spraying-Ilayaraja-low
FID6292 | Plumbing & Sanitary | Scrub Sink | Other: Panel coming out | Affecting Public | RMG > RH > 7 > OR7&8 Scrub Rm |  | 2022-01-18 14:14:04 | 2022-01-19 11:30:44 | 2022-01-19 11:31:23 | 2022-01-19 11:32:17 | 2022-01-19 11:32:58 | 2022-01-19 11:35:30 | Hossain | onside found OR- 7 Scrub room basin sensor panel came off. Fixed the sensor panel as per their request. | [6 empty] | Sensor panel coming out-Hossain-low
FID6291 | Mechanical | Lift & Escalators | System Shows fault / Error code | Affecting Public | RMG > RSC > 1 > Lobby |  | 2022-01-18 13:37:40 | 2022-01-19 11:28:09 | 2022-01-19 11:28:28 | 2022-01-19 11:28:48 | 2022-01-19 11:29:09 | 2022-01-19 11:29:40 | Chang Fook Keong Alan | I have reset back | [6 empty] | Escalator not working-Allan-low
FID6290 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > 25 Tannery Lane > 7 > TL-7-27 Office |  | 2022-01-18 13:28:55 | 2022-01-28 13:34:58 | 2022-01-28 13:35:23 | 2022-01-28 13:35:44 | 2022-01-28 13:44:17 | 2022-01-28 13:44:43 | FRC | Replaced new light | [6 empty] | Light fused-ela-low
FID6289 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > Operating Theatre 8 |  | 2022-01-18 13:27:22 | 2022-01-18 13:31:37 | 2022-01-18 13:31:58 | 2022-01-18 13:35:18 | 2022-01-18 13:35:49 | 2022-01-18 13:52:45 | FRC | Temperature setpoint is 28c and heater manually 0%. Adjusted the heater from 0% to 60% in bms system make it warm | [6 empty] | Aircon make it warm-su-low
FID6288 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Affecting Public | RMG > RH > 2 > Healthcheck Consult Rm 6 |  | 2022-01-18 13:23:15 | 2022-01-18 16:00:45 | 2022-01-18 16:01:10 | 2022-01-18 16:23:03 | 2022-01-18 16:26:10 | 2022-01-18 16:27:44 | Arasan Balasubramanian | adjusted the airflow | [6 empty] | Airflow too strong-a.bala-low
FID6287 | Building | Door Stopper | Missing | Affecting Public | RMG > RH > 1 > Nuclear Med MRI |  | 2022-01-18 13:22:27 | 2022-01-28 12:00:49 | 2022-01-28 12:01:59 | 2022-01-28 12:02:40 | 2022-01-28 12:03:02 | 2022-02-07 14:51:57 | FRC | Fixed new door stopper | [6 empty] | No door stopper-murugan-low
FID6278 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 1 > A&E Bed 9 |  | 2022-01-18 09:53:52 | 2022-01-28 10:47:48 | 2022-01-28 11:53:51 | 2022-01-28 11:54:14 | 2022-01-28 11:54:37 | 2022-01-28 11:55:21 | FRC | Adjusted AHU 1-3 temperature setpoint from 20c to 21.5c in bms system make it warm slightly | [6 empty] | Aircon too cold, make it warm-Jailani-low
FID6277 | Mechanical | Autodoor | Cannot Open or Close | Affecting Public | RMG > RSC > 9 > Fireman Lift Lobby |  | 2022-01-18 09:52:58 | 2022-01-28 10:44:51 | 2022-01-28 10:45:24 | 2022-01-28 10:45:44 | 2022-01-28 10:46:04 | 2022-01-28 10:46:31 | FRC | Reset the door power back to normal | [6 empty] | Auto door cannot close-a.bala-low
FID6276 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 7 > Operating Theatre 4 |  | 2022-01-18 09:37:06 | 2022-01-19 11:37:18 | 2022-01-19 16:00:57 | 2022-01-19 16:01:17 | 2022-01-19 16:01:39 | 2022-01-28 10:28:53 | FRC | Reset the alarm back to normal | [6 empty] | Medical air gas panel alarming-Hossain-medium
FID6272 | Office and Furniture | Cabinet | Cannot open / close | Affecting Public | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-18 09:22:26 | 2022-01-18 14:57:07 | 2022-01-18 14:58:55 | 2022-01-18 14:59:57 | 2022-01-28 10:27:23 | 2022-01-28 10:27:54 | FRC | Opened the locker as per staff request | [6 empty] | Locker cannot open-ilayaraja-low
FID6271 | Mechanical | AHU / FCU / CU | Other: Aircon smelly | Affecting Public | RMG > RH > 7 > Day Surgery |  | 2022-01-18 09:21:44 | 2022-01-28 10:19:28 | 2022-01-28 10:19:54 | 2022-01-28 10:20:18 | 2022-01-28 10:21:11 | 2022-01-28 10:26:32 | FRC | Checked onsite, there is no smell. Informed to user. | [6 empty] | Aircon smelly-Jailani-low
FID6270 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > Healthcheck Consult Rm 6 |  | 2022-01-18 09:20:49 | 2022-01-18 09:37:35 | 2022-01-18 09:37:55 | 2022-01-18 09:38:16 | 2022-01-18 09:38:38 | 2022-01-18 09:49:51 | FRC | Adjusted VAV 1-1-2 temperature setpoint from 24c to 22c and damper position from 60% manual to 80% manual in bms system | [6 empty] | Aircon make it cool-su-low
FID6265 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-18 08:28:44 | 2022-01-18 08:30:27 | 2022-01-18 08:30:54 | 2022-01-18 08:31:28 | 2022-01-18 08:31:44 | 2022-01-18 08:32:40 | Rajendran Manikandan | adjusted the temperature from bms system make it warm | [6 empty] | Aircon make it warm-mani-low
FID6264 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-18 08:22:10 | 2022-01-18 08:26:18 | 2022-01-18 08:27:33 | 2022-01-18 08:28:52 | 2022-01-18 08:29:13 | 2022-01-18 08:29:40 | Rajendran Manikandan | Reset normal back | [6 empty] | Oxygen panel alarming -mani-high
FID6262 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 854 |  | 2022-01-18 08:15:51 | 2022-01-27 17:34:09 | 2022-01-27 17:34:30 | 2022-01-27 17:34:51 | 2022-01-27 17:35:11 | 2022-01-27 17:35:43 | FRC | Adjusted the aircon make it cool | [6 empty] | Aircon make it cool-aru-low
FID6260 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > Main Lobby |  | 2022-01-18 07:45:30 | 2022-01-18 07:59:00 | 2022-01-18 07:59:26 | 2022-01-18 07:59:55 | 2022-01-18 08:16:03 | 2022-01-18 08:17:20 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low
FID6259 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 9 > Nursing Stn B |  | 2022-01-18 07:42:13 | 2022-01-27 17:30:16 | 2022-01-27 17:31:03 | 2022-01-27 17:31:25 | 2022-01-27 17:31:48 | 2022-01-27 17:32:48 | FRC | Adjusted the aircon make it warm | [6 empty] | Aircon make it warm-aru-low
FID6258 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1365-1370 |  | 2022-01-18 07:40:19 | 2022-01-27 17:26:38 | 2022-01-27 17:26:59 | 2022-01-27 17:27:21 | 2022-01-27 17:27:43 | 2022-01-27 17:28:23 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6257 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-18 07:37:56 | 2022-01-27 17:21:58 | 2022-01-27 17:22:20 | 2022-01-27 17:24:51 | 2022-01-27 17:25:13 | 2022-01-27 17:25:51 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6254 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 13 > Ward 1319-1327 Nurse Station |  | 2022-01-17 22:57:57 | 2022-01-18 01:26:11 | 2022-01-18 07:55:55 | 2022-01-18 07:56:32 | 2022-01-18 07:57:01 | 2022-01-18 07:58:10 | Rajendran Manikandan | clearly the choke | [6 empty] | Basin choke -mani-low
FID6253 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2022-01-17 22:55:37 | 2022-01-17 23:01:52 | 2022-01-17 23:02:14 | 2022-01-17 23:02:27 | 2022-01-17 23:02:38 | 2022-01-17 23:03:25 | Rajendran Manikandan | replaced 1 nos cylinder | [6 empty] | Need 1 big co2 cylinder-mani-medium
FID6251 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Nuclear Med Counter |  | 2022-01-17 22:45:40 | 2022-01-17 22:59:01 | 2022-01-17 22:59:26 | 2022-01-17 22:59:46 | 2022-01-17 22:59:50 | 2022-01-17 23:01:24 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low
FID6244 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RH > 10 > Handicap Toilet |  | 2022-01-17 17:40:06 | 2022-01-19 11:32:07 | 2022-01-19 11:32:26 | 2022-01-19 11:32:51 | 2022-01-19 11:38:16 | 2022-01-19 11:38:56 | Chang Fook Keong Alan | I have cleared the Chok |  |  |  |  | 1 |  | Toilet bowl choke-Allan-low
FID6243 | Building | Door Closer | Unable to open or close properly | More than 1 room | RMG > RSC > 16 > Eye Centre Consult Rm 6 |  | 2022-01-17 17:37:26 | 2022-01-19 12:15:01 | 2022-01-19 12:15:22 | 2022-01-19 12:15:30 | 2022-01-19 12:16:01 | 2022-01-19 12:18:54 | Hossain | onsite check & found door arm dislodge. Fixed back properly the door arm back to normal. |  |  |  |  | 1 |  | Door cannot close properly-Hossain-low
FID6242 | Medical Equipment | Commode Chair | Other: arm rest loose | More than 1 room | RMG > RH > 10 > Nursing Stn B |  | 2022-01-17 16:56:59 | 2022-01-27 17:19:10 | 2022-01-27 17:19:31 | 2022-01-27 17:19:54 | 2022-01-27 17:20:17 | 2022-01-27 17:20:52 | FRC | Tighten the wheelchair arm rest |  |  |  |  | 1 |  | Wheel chair arm rest loose-Nazri-low
FID6241 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | More than 1 room | RMG > RH > 2 > L2 Male Toilet |  | 2022-01-17 16:17:55 | 2022-01-17 19:55:30 | 2022-01-17 19:55:58 | 2022-01-17 19:56:24 | 2022-01-17 19:56:48 | 2022-01-17 19:57:35 | Vadivelu Balasubramanian | urinal choke cleared |  |  |  |  | 1 |  | Toilet bowl choke-V.Bala-low
FID6240 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 10 > Doctor's Lounge |  | 2022-01-17 16:15:33 | 2022-01-19 11:39:44 | 2022-01-19 11:40:04 | 2022-01-19 11:40:22 | 2022-01-19 11:40:40 | 2022-01-19 11:41:29 | Chang Fook Keong Alan | I have changed the bulb |  |  |  |  | 1 |  | Light flickering-Allan-low
FID6238 | Medical Equipment | Hygrometer | Other: humitity out of range | More than 1 room | RMG > RH > 7 > Angio Suite |  | 2022-01-17 15:53:24 | 2022-01-27 17:05:59 | 2022-01-27 17:06:33 | 2022-01-27 17:06:53 | 2022-01-27 17:07:14 | 2022-01-27 17:18:33 | FRC | Adjusted the temperature for the AHU 7-11 to reduce the humidity |  |  |  |  | 1 |  | Humidity out of range-Jailani-low
FID6237 | Office and Furniture | TV | Cannot operate / defective | More than 1 room | RMG > RH > 10 > Ward 1050 |  | 2022-01-17 15:29:25 | 2022-01-19 12:27:45 | 2022-01-27 17:03:05 | 2022-01-27 17:03:55 | 2022-01-27 17:04:17 | 2022-01-27 17:05:14 | FRC | TV remote faulty. No spare remote. Informed to staff to use other room spare tv remote. |  |  |  |  | 1 |  | TV remote not working-hossain-low
FID6236 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Day Surgery |  | 2022-01-17 15:26:39 | 2022-01-27 16:55:05 | 2022-01-27 16:56:06 | 2022-01-27 16:56:26 | 2022-01-27 16:57:25 | 2022-01-27 16:58:34 | FRC | Replaced new light |  |  |  |  | 1 |  | Light flickering-nazri-low
FID6230 | Building | Door Knob / Handle | Unable to open or close properly | More than 1 room | RMG > RSC > 8 > Children Centre Consult Rm 3 |  | 2022-01-17 14:26:43 | 2022-01-27 16:59:16 | 2022-01-27 16:59:37 | 2022-01-27 17:00:03 | 2022-01-27 17:00:35 | 2022-01-27 17:01:17 | FRC | Tighten the door handle |  |  |  |  | 1 |  | Door handle spoilt-nazri-low
FID6228 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-17 14:08:54 | 2022-01-19 11:42:36 | 2022-01-19 11:42:55 | 2022-01-19 11:43:14 | 2022-01-19 11:43:33 | 2022-01-19 11:44:12 | Chang Fook Keong Alan | I have make it cool |  |  |  |  | 1 |  | Aircon make it cool-Allan-low
FID6227 | Plumbing & Sanitary | Water Heater | No water | More than 1 room | RMG > RH > 8 > Ward 855 |  | 2022-01-17 14:04:55 | 2022-01-19 11:44:43 | 2022-01-19 11:45:01 | 2022-01-19 11:45:25 | 2022-01-19 11:45:45 | 2022-01-19 11:46:34 | Chang Fook Keong Alan | Water heater Back to normal |  |  |  |  | 1 |  | No hot water-Allan-low
FID6223 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Ward 855 |  | 2022-01-17 12:03:56 | 2022-01-17 13:09:30 | 2022-01-17 13:09:51 | 2022-01-17 13:10:10 | 2022-01-17 13:10:29 | 2022-01-17 13:11:12 | Chang Fook Keong Alan | We have made it hot | [6 empty] | Hot water no coming-Allan-low
FID6222 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > Nuclear Medicine Centre |  | 2022-01-17 12:00:18 | 2022-01-17 12:01:12 | 2022-01-17 12:01:52 | 2022-01-17 12:02:43 | 2022-01-17 12:03:45 | 2022-01-17 12:06:17 | Arasan Balasubramanian | replaced new light bulb | [6 empty] | Light fused-a.bala-low
FID6220 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Ward 849 |  | 2022-01-17 11:56:08 | 2022-01-17 13:11:42 | 2022-01-17 13:12:14 | 2022-01-17 13:12:34 | 2022-01-17 13:12:52 | 2022-01-17 13:13:39 | Chang Fook Keong Alan | We have made it hot the water | [6 empty] | Hot water no coming-Allan-low
FID6193 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Operating Theatre 9 |  | 2022-01-17 08:05:21 | 2022-01-17 08:24:58 | 2022-01-17 08:25:56 | 2022-01-17 08:26:31 | 2022-01-17 08:27:13 | 2022-01-17 08:41:02 | Muthu Sathasivam | before adjusted vsd to 50% for ot door replacement change vsd control to 70% | [6 empty] | Need to adjust the aircon make cool-satha-low
FID6192 | Office and Furniture | Cabinet | Cannot open / close | More than 1 room | RMG > RH > 10 > Business Centre |  | 2022-01-17 07:59:42 | 2022-01-17 08:09:08 | 2022-01-17 08:10:10 | 2022-01-17 08:10:39 | 2022-01-17 08:11:12 | 2022-01-17 08:14:06 | Sivalingam Ilayaraja | thighend the screw then normal back | [6 empty] | Cabinet drawer can't close-ilayaraja-low
FID6190 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1050 |  | 2022-01-17 02:12:18 | 2022-01-17 02:13:54 | 2022-01-17 02:14:15 | 2022-01-17 02:14:36 | 2022-01-17 02:14:56 | 2022-01-17 02:16:08 | Muthu Sathasivam | checked on bms temperature setpoint set to 21 degrees manually change to auto | [6 empty] | Aircon make it warm-satha-low
FID6184 | Medical Equipment | Medical Gas | Other: oxygen meter have alarm | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-17 00:55:50 | 2022-01-17 00:56:56 | 2022-01-17 00:57:17 | 2022-01-17 00:57:39 | 2022-01-17 00:59:57 | 2022-01-17 01:01:01 | Muthu Sathasivam | reset back to normal | [6 empty] | Oxygen panel alarming-satha-high
FID6183 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1029 |  | 2022-01-17 00:52:39 | 2022-01-17 00:58:25 | 2022-01-17 01:01:40 | 2022-01-17 01:02:22 | 2022-01-17 01:02:55 | 2022-01-17 01:04:52 | Muthu Sathasivam | all settings are ok working normal | [6 empty] | Aircon make cool-satha-low
FID6182 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1038 |  | 2022-01-16 22:45:29 | 2022-01-16 23:00:22 | 2022-01-16 23:01:08 | 2022-01-16 23:01:52 | 2022-01-16 23:06:18 | 2022-01-16 23:08:06 | Muthu Sathasivam | damper position manually 100%in bms change to auto | [6 empty] | Aircon make it warm-satha-low
FID6180 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E |  | 2022-01-16 22:21:05 | 2022-01-16 22:22:30 | 2022-01-16 22:22:53 | 2022-01-16 22:23:17 | 2022-01-16 22:23:38 | 2022-01-16 22:24:06 | Muthu Sathasivam | replace new bulb | [6 empty] | Light spoilt near sliding door-satha-low
FID6178 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1038 |  | 2022-01-16 19:46:33 | 2022-01-16 19:47:56 | 2022-01-16 19:48:17 | 2022-01-16 19:48:34 | 2022-01-16 19:48:38 | 2022-01-16 19:50:34 | Rajendran Manikandan | adjusted the temperature setpoint 20c and damper position 100% bms system make it cool | [6 empty] | Aircon make it cool-mani-low
FID6175 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU |  | 2022-01-16 17:09:53 | 2022-01-27 16:35:37 | 2022-01-27 16:35:59 | 2022-01-27 16:37:40 | 2022-01-27 16:38:01 | 2022-01-27 16:38:37 | FRC | Adjusted the temperature in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID6174 | Building | Door Knob / Handle | Noisy | Localised to room | RMG > RH > 8 > Ward 850 |  | 2022-01-16 17:07:00 | 2022-01-16 17:20:49 | 2022-01-16 17:21:08 | 2022-01-16 17:21:31 | 2022-01-16 17:22:01 | 2022-01-16 17:22:35 | Chang Fook Keong Alan | I have tighten back the screw | [6 empty] | Door loose-allan-low
FID6163 | Plumbing & Sanitary | Hot Water System | No water | Affecting Public | RMG > RH > 10 > Ward 1010 |  | 2022-01-16 09:24:08 | 2022-01-16 17:23:47 | 2022-01-16 17:24:11 | 2022-01-16 17:24:32 | 2022-01-16 17:24:53 | 2022-01-16 17:25:25 | Chang Fook Keong Alan | The water is hot now | [6 empty] | No hot water in shower-Allan-low
FID6162 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1045 |  | 2022-01-16 08:23:05 | 2022-01-16 08:24:14 | 2022-01-16 08:24:50 | 2022-01-16 08:25:11 | 2022-01-16 08:25:40 | 2022-01-16 08:26:41 | Muthu Sathasivam | damper position have set manually to 65% change to auto | [6 empty] | Need to off the aircon-satha-low
FID6161 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Delivery Suite 7 |  | 2022-01-16 08:13:33 | 2022-01-17 00:59:00 | 2022-01-17 00:59:30 | 2022-01-17 01:00:00 | 2022-01-17 01:00:42 | 2022-01-17 01:01:56 | Sivalingam Ilayaraja | open the hot water line valve | [6 empty] | No hot water-ilayaraja-low
FID6160 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-16 08:11:41 | 2022-01-17 01:02:59 | 2022-01-17 01:03:29 | 2022-01-17 01:03:57 | 2022-01-17 07:28:30 | 2022-01-17 07:29:21 | Sivalingam Ilayaraja | cleared the chock | [6 empty] | Basin choke-ilayaraja-low
FID6159 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 709 |  | 2022-01-16 02:56:25 | 2022-01-16 02:57:27 | 2022-01-16 03:01:03 | 2022-01-16 03:01:31 | 2022-01-16 03:02:00 | 2022-01-16 03:02:39 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Aircon make it warm-satha-low
FID6158 | Building | Door Knob / Handle | Misaligned / dangling | More than 1 room | RMG > RH > 11 > Level 11 |  | 2022-01-16 02:54:43 | 2022-01-16 02:57:59 | 2022-01-16 02:58:27 | 2022-01-16 02:58:52 | 2022-01-16 02:59:15 | 2022-01-16 03:00:20 | Muthu Sathasivam | screw loose and misaligned tighten the screw working norma | [6 empty] | Door handle spoilt in main door entrance-satha-low
FID6152 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 10 > Ward 1058 |  | 2022-01-15 20:20:38 | 2022-01-15 20:25:37 | 2022-01-15 20:26:00 | 2022-01-15 20:26:25 | 2022-01-15 20:26:46 | 2022-01-15 20:27:18 | Rajendran Manikandan | Reset normal back | [6 empty] | Safe bax cannot open-mani-low
FID6151 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 1 > A&E |  | 2022-01-15 19:47:25 | 2022-01-27 16:31:56 | 2022-01-27 16:32:17 | 2022-01-27 16:32:42 | 2022-01-27 16:33:05 | 2022-01-27 16:33:34 | FRC | Replaced new oxygen cylinders | [6 empty] | Need 3 takeo 0.4 ,1.0,0.8 oxygen cylinder -aru-medium
FID6150 | Mechanical | Autodoor | Cannot Open or Close | Localised to room | RMG > RSC > 9 > Fireman Lift Lobby |  | 2022-01-15 19:37:49 | 2022-01-15 19:52:05 | 2022-01-15 19:52:26 | 2022-01-15 19:52:49 | 2022-01-15 19:53:24 | 2022-01-15 19:54:00 | Rajendran Manikandan | Power Reset normal back | [6 empty] | Auto door cannot close -mani-low
FID6149 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 Nurse Station |  | 2022-01-15 19:34:45 | 2022-01-27 16:26:13 | 2022-01-27 16:26:34 | 2022-01-27 16:27:13 | 2022-01-27 16:29:21 | 2022-01-27 16:29:58 | FRC | Adjusted the temperature in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID6148 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-15 19:32:48 | 2022-01-15 19:48:22 | 2022-01-15 19:49:31 | 2022-01-15 19:49:49 | 2022-01-15 19:50:00 | 2022-01-15 19:51:30 | Rajendran Manikandan | adjusted the temperature setpoint form 22c to 18c bms system make it cool | [6 empty] | Aircon make it cool-mani-low
FID6145 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2022-01-15 15:46:23 | 2022-01-15 15:54:59 | 2022-01-15 15:55:18 | 2022-01-15 15:55:22 | 2022-01-15 15:56:26 | 2022-01-15 15:57:57 | Rajendran Manikandan | Reset normal back | [6 empty] | Safe box cannot open-mani-low
FID6144 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2022-01-15 15:43:31 | 2022-01-15 15:52:23 | 2022-01-15 15:52:37 | 2022-01-15 15:52:51 | 2022-01-15 15:53:16 | 2022-01-15 15:54:30 | Rajendran Manikandan | adjusted the temperature setpoint form20c to 18c bms system make it cool | [6 empty] | Aircon make it cool-mani-low
FID6143 | Medical Equipment | Patient Bed | Other: bed button not working | Localised to room | RMG > RH > 13 > Ward 1358-1363 |  | 2022-01-15 15:41:58 | 2022-01-17 12:02:50 | 2022-01-27 16:22:57 | 2022-01-27 16:23:26 | 2022-01-27 16:23:47 | 2022-01-27 16:25:36 | FRC | Bed remote lock. Unlock the remote and adjusted the bed. | [6 empty] | Bed button not working -ming cai-low
FID6142 | Building | Door Closer | Misaligned / dangling | Localised to room | RMG > RSC > 13 > Fireman Lift Lobby |  | 2022-01-15 15:36:02 | 2022-01-15 15:46:30 | 2022-01-15 15:46:58 | 2022-01-15 15:47:24 | 2022-01-15 15:47:43 | 2022-01-15 15:48:31 | Rajendran Manikandan | n | [6 empty] | Door cannot close properly-mani-low
FID6140 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 9 |  | 2022-01-15 14:21:17 | 2022-01-15 14:23:02 | 2022-01-15 14:23:47 | 2022-01-15 14:24:30 | 2022-01-15 14:24:54 | 2022-01-15 14:26:55 | Rajendran Manikandan | adjusted the temperature setpoint form 18c to 16c form bms system make it cool | [6 empty] | Aircon make it cool-mani-low
FID6131 | Office and Furniture | Safe Box | Cannot open / close | Affecting Public | RMG > RH > 10 > Ward 1058 |  | 2022-01-15 10:25:54 | 2022-01-15 10:31:52 | 2022-01-15 10:32:20 | 2022-01-15 10:32:40 | 2022-01-15 10:33:00 | 2022-01-15 10:34:10 | Li Fei | safe box swopped with 1039. patient admitted at night time. safebox at 1039 settled | [6 empty] | Safe box cannot open-a.bala-low
FID6130 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 911 |  | 2022-01-15 10:25:00 | 2022-01-27 16:17:52 | 2022-01-27 16:20:28 | 2022-01-27 16:20:50 | 2022-01-27 16:21:28 | 2022-01-27 16:22:00 | FRC | Replaced new light | [6 empty] | Ceiling light fused-a.bala-low
FID6129 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn C |  | 2022-01-15 10:23:27 | 2022-01-27 16:14:52 | 2022-01-27 16:15:34 | 2022-01-27 16:16:23 | 2022-01-27 16:16:44 | 2022-01-27 16:17:14 | FRC | Adjusted the aircon temperature in bms system make it cool | [6 empty] | Aircon make it cool-v.bala-low
FID6128 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 8 > Ward 819 |  | 2022-01-15 10:21:43 | 2022-01-27 16:12:20 | 2022-01-27 16:12:40 | 2022-01-27 16:13:04 | 2022-01-27 16:13:32 | 2022-01-27 16:14:11 | FRC | Manually open the diffuser onsite make it cool | [6 empty] | Aircon make it cool-v.bala-low
FID6127 | Electrical | Call System | Other: Call bell keep ringing | Affecting Public | RMG > RH > 9 > Ward 926 |  | 2022-01-15 10:20:36 | 2022-01-15 10:35:00 | 2022-01-15 10:35:21 | 2022-01-15 10:35:40 | 2022-01-15 10:36:01 | 2022-01-15 10:36:29 | Li Fei | pillow speaker cable broken | [6 empty] | Call bell keep ringing-A.bala-low
FID6126 | Plumbing & Sanitary | Hot Water System | Other: no hot water | Affecting Public | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-15 10:19:41 | 2022-01-27 16:08:57 | 2022-01-27 16:09:18 | 2022-01-27 16:09:37 | 2022-01-27 16:11:06 | 2022-01-27 16:11:32 | FRC | No hot water due to circulation pump faulty. Rectified the circulation pump, back to normal. Hot water working | [6 empty] | No hot water-ming cai-low
FID6125 | Plumbing & Sanitary | Hot Water System | Other: Water not hot | Affecting Public | RMG > RH > 7 > OT Male Channing Rm |  | 2022-01-15 10:19:00 | 2022-01-27 15:09:05 | 2022-01-27 15:09:28 | 2022-01-27 15:31:32 | 2022-01-27 15:31:53 | 2022-01-27 15:54:33 | FRC | No hot water due to circulation pump faulty. Rectified the circulation pump, back to normal. Hot water working | [6 empty] | No hot water-ming cai-low
FID6124 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RH > 9 > Ward 971 - 972 |  | 2022-01-15 10:18:04 | 2022-01-15 11:38:59 | 2022-01-15 11:39:44 | 2022-01-15 11:40:16 | 2022-01-15 11:43:06 | 2022-01-15 12:08:54 | Rajendran Manikandan | 972 tv faulty and temporary swop from room 970 | [6 empty] | TV not working-mani-low
FID6123 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 10 > Ward 1039 |  | 2022-01-15 10:17:19 | 2022-01-15 12:09:29 | 2022-01-15 12:09:57 | 2022-01-15 12:10:22 | 2022-01-15 12:10:44 | 2022-01-15 12:11:14 | Rajendran Manikandan | Reset normal back | [6 empty] | Safe box cannot lock-mani-low
FID6118 | Mechanical | Pneumatic Tube | Missing | More than 1 room | RMG > RH > 1 > A&E |  | 2022-01-15 07:49:45 | 2022-01-27 15:00:22 | 2022-01-27 15:00:47 | 2022-01-27 15:01:09 | 2022-01-27 15:01:29 | 2022-01-27 15:05:41 | FRC | Purge the system, found the tube and return to user |  |  |  |  | 1 |  | Pneumatic tube missing-a.bala-medium
FID6098 | Electrical | Call System | Unserviceable | More than 1 room | RMG > RH > 9 > Ward 917 |  | 2022-01-14 20:20:25 | 2022-01-15 11:17:48 | 2022-01-15 11:18:16 | 2022-01-15 11:18:39 | 2022-01-15 11:19:02 | 2022-01-15 11:19:45 | Li Fei | Nurse call pillow speaker cable broken. Need to repalce new pillow speaker | [6 empty] | Nurse call bell non-stop ringing-Aru-low
FID6097 | Plumbing & Sanitary | Hot Water System | No water | More than 1 room | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-14 20:14:47 | 2022-01-14 20:21:16 | 2022-01-14 20:26:03 | 2022-01-14 20:31:19 | 2022-01-14 20:31:52 | 2022-01-14 20:33:08 | Sivalingam Ilayaraja | on the hot water valve | [6 empty] | Need to check the hot water pipe line-Ilayaraja-low
FID6095 | Office and Furniture | Wall Clock | Chipped / Cracked | More than 1 room | RMG > RH > 8 > Ward 819 |  | 2022-01-14 18:04:02 | 2022-01-14 20:37:22 | 2022-01-14 20:37:52 | 2022-01-14 20:38:26 | 2022-01-14 20:38:47 | 2022-01-14 20:39:30 | Rajendran Manikandan | Replaced new battery | [6 empty] | Wall clock not working-mani-low
FID6094 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > Angio Control Rm |  | 2022-01-14 17:58:55 | 2022-01-27 14:54:18 | 2022-01-27 14:55:17 | 2022-01-27 14:55:36 | 2022-01-27 14:58:43 | 2022-01-27 14:59:22 | FRC | Adjusted AHU 7-11 temperature setpoint in bms system to reduce the humidity | [6 empty] | Aircon humidity out of range-satha-low
FID6092 | Office and Furniture | Fax Machine | Other: no working | Affecting Public | RMG > RH > 7 > Clinical Lab |  | 2022-01-14 16:26:55 | 2022-01-14 16:28:23 | 2022-01-14 16:28:51 | 2022-01-14 16:29:13 | 2022-01-14 16:29:40 | 2022-01-14 20:40:47 | Rajendran Manikandan | line problem and normal back | [6 empty] | Fax machine no working-mani-low
FID6091 | Medical Equipment | Fridges & Freezers | Leaking | Localised to room | RMG > RH > 8 > Ward 819 |  | 2022-01-14 16:25:07 | 2022-01-14 16:31:25 | 2022-01-14 16:31:55 | 2022-01-14 16:32:27 | 2022-01-14 16:32:53 | 2022-01-14 16:34:05 | Muthu Sathasivam | fridge have spoiled and swap the fridge from 821 to 819 | [6 empty] | Fridge faulty-satha-low
FID6087 | Medical Equipment | Medical Gas | Change Cylinders | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-14 15:29:52 | 2022-01-14 15:30:10 | 2022-01-14 15:30:47 | 2022-01-14 15:31:25 | 2022-01-14 15:41:06 | 2022-01-14 15:41:37 | Muthu Shanmugavelu | replaced 4 nos cylinders | [6 empty] | Need 4 takeo 1.0 cylinders-shanmu, ilayaraja-medium
FID6079 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn C |  | 2022-01-14 14:07:59 | 2022-01-14 16:03:27 | 2022-01-14 16:04:25 | 2022-01-14 16:05:20 | 2022-01-14 16:05:49 | 2022-01-14 16:07:53 | Sivalingam Ilayaraja | adjested the temprature from bms then make it cool | [6 empty] | Aircon too hot, make it cool-Ilayaraja-low
FID6078 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | More than 1 room | RMG > RH > 8 > Ward 813 (Pead's Isolation) |  | 2022-01-14 13:49:09 | 2022-01-14 15:12:41 | 2022-01-14 15:13:32 | 2022-01-14 15:14:11 | 2022-01-14 15:14:49 | 2022-01-14 15:18:24 | Sivalingam Ilayaraja | adjested the temprature from bms then make it cool | [6 empty] | Isolation room display panel alarming-Jailani-low
FID6077 | Mechanical | Pneumatic Tube | Missing | More than 1 room | RMG > RH > 2 > RM@RH |  | 2022-01-14 13:34:18 | 2022-01-14 13:35:04 | 2022-01-14 13:35:35 | 2022-01-14 13:35:57 | 2022-01-14 13:41:59 | 2022-01-14 13:43:02 | Muthu Shanmugavelu | found one tube at station 82 | [6 empty] | Pneumatic Tube missing-Shanmu-low
FID6076 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Housekeeping Office |  | 2022-01-14 12:38:31 | 2022-01-14 13:51:39 | 2022-01-14 13:52:11 | 2022-01-14 13:53:06 | 2022-01-14 13:53:25 | 2022-01-14 13:55:39 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light fused-mani-low
FID6075 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | Localised to room | RMG > RH > 8 > Ward 813 (Pead's Isolation) |  | 2022-01-14 12:33:43 | 2022-01-14 12:34:24 | 2022-01-14 12:40:06 | 2022-01-14 12:40:18 | 2022-01-14 12:41:14 | 2022-01-14 12:48:30 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Aircon make cool-satha-low
FID6074 | Mechanical | Air Diffuser (supply/return) | Other: return air grill black colour things drop down | Localised to room | RMG > RSC > 8 > Children Centre Consult Rm 8 |  | 2022-01-14 12:28:57 | 2022-01-14 12:31:49 | 2022-01-14 12:42:08 | 2022-01-14 12:42:58 | 2022-01-14 12:43:49 | 2022-01-14 12:47:22 | Muthu Sathasivam | close with filter | [6 empty] | Aircon vent dust come down-satha-low
FID6070 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > ESWL |  | 2022-01-14 11:56:45 | 2022-01-14 11:58:44 | 2022-01-14 11:59:01 | 2022-01-14 11:59:21 | 2022-01-14 12:08:31 | 2022-01-14 12:09:28 | Muthu Shanmugavelu | Delivered 1 O2 cylinder | [6 empty] | Need 1 o2 cylinder-shanmu-medium
FID6065 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 12 > Women Centre |  | 2022-01-14 10:59:30 | 2022-01-14 11:09:52 | 2022-01-14 11:10:37 | 2022-01-14 11:11:09 | 2022-01-14 11:13:46 | 2022-01-14 11:14:41 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light fused-mani-low
FID6064 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-14 10:12:19 | 2022-01-14 10:13:44 | 2022-01-14 10:16:43 | 2022-01-14 10:17:40 | 2022-01-14 10:18:31 | 2022-01-14 10:20:03 | Sivalingam Ilayaraja | adjested the temprature from bms then make it cool. | [6 empty] | Aircon make it cool-ilayaraja-low
FID6063 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1057 |  | 2022-01-14 09:56:52 | 2022-01-14 10:06:36 | 2022-01-14 10:07:15 | 2022-01-14 10:07:52 | 2022-01-14 10:08:34 | 2022-01-14 10:10:08 | Sivalingam Ilayaraja | adjested the temprature from bms make it warm | [6 empty] | Need to adjust aircon make it warm-ilayaraja-low
FID6047 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-14 01:01:21 | 2022-01-14 01:02:22 | 2022-01-14 01:02:52 | 2022-01-14 01:03:22 | 2022-01-14 01:03:59 | 2022-01-14 01:05:44 | Arasan Balasubramanian | adjusted the temprature aircon make it cold |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID6046 | Office and Furniture | Wall Clock | Other: battery change | More than 1 room | RMG > RH > 9 > Ward 976 - 977 |  | 2022-01-14 00:59:22 | 2022-01-14 12:17:43 | 2022-01-14 12:18:25 | 2022-01-14 12:18:50 | 2022-01-14 12:19:14 | 2022-01-14 12:19:49 | Vadivelu Balasubramanian | replaced battery |  |  |  |  | 1 |  | Wall clock battery need to change-V.Bala-low
FID6045 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1028 |  | 2022-01-13 22:35:39 | 2022-01-14 12:20:34 | 2022-01-14 12:21:05 | 2022-01-14 12:21:32 | 2022-01-14 12:21:59 | 2022-01-14 12:23:54 | Vadivelu Balasubramanian | adjusted temperature in bms vav control damper position 20to7o make it cool |  |  |  |  | 1 |  | Aircon make cool-V.Bala-low
FID6042 | Plumbing & Sanitary | Bidet spray / Hose | Leaking | Localised to room | RMG > RSC > 8 > Handicap Toilet |  | 2022-01-13 19:02:56 | 2022-01-19 12:33:19 | 2022-01-19 12:33:39 | 2022-01-19 12:34:02 | 2022-01-19 12:34:13 | 2022-01-19 12:35:34 | Hossain | onsite check & replaced the bidet spray hose back to normal. | [6 empty] | Bidet spray leaking-hossain-low
FID6040 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 923 |  | 2022-01-13 18:35:39 | 2022-01-13 18:56:20 | 2022-01-13 18:56:43 | 2022-01-13 18:57:02 | 2022-01-13 18:57:23 | 2022-01-13 18:58:17 | Chang Fook Keong Alan | Have replace new bulb | [6 empty] | Light spoilt-allan-low
FID6034 | Electrical | Light Bulb | Other: not same type so replace to same type | Localised to room | RMG > RH > 8 > Ward 833 (Victoria Suite) |  | 2022-01-13 16:37:18 | 2022-01-27 14:47:51 | 2022-01-27 14:51:17 | 2022-01-27 14:51:38 | 2022-01-27 14:51:58 | 2022-01-27 14:52:23 | FRC | Replaced new light | [6 empty] | Need to change 4 nos 865 light-Ming cai-low
FID6030 | Plumbing & Sanitary | Scrub Sink | Water flowing non-stop | Localised to room | RMG > RH > 7 > OR4&5 Scrub Rm |  | 2022-01-13 15:39:16 | 2022-01-13 15:39:41 | 2022-01-13 15:39:59 | 2022-01-13 15:40:17 | 2022-01-13 15:40:36 | 2022-01-13 19:48:42 | Muthu Shanmugavelu | Aca contractor replaced sensor for 1 Bay at OT4 | [6 empty] | ACA contractor replacing sensors for scrub sinks-Shanmu-low
FID6029 | Mechanical | Air Diffuser (supply/return) | Chipped / Cracked | More than 1 room | RMG > RH > 13 > Business Office |  | 2022-01-13 15:28:11 | 2022-01-13 22:39:27 | 2022-01-13 22:39:51 | 2022-01-13 22:40:20 | 2022-01-13 22:40:44 | 2022-01-13 22:41:13 | Muthu Sathasivam | diffuser fix back | [6 empty] | Aircon diffuser came out, need to check-satha-low
FID6028 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > A&E Critical Care Counter |  | 2022-01-13 15:17:14 | 2022-01-13 15:17:42 | 2022-01-13 15:18:05 | 2022-01-13 15:18:40 | 2022-01-13 15:19:03 | 2022-01-13 15:20:22 | Rajendran Manikandan | replaced new lights | [6 empty] | ceiling light fused-Ilayaraja-low
FID6025 | Office and Furniture | Safe Box | Cannot open / close | More than 1 room | RMG > RH > 2 > RJC Treatment Rm 6 |  | 2022-01-13 14:51:24 | 2022-01-19 11:50:04 | 2022-01-19 11:50:24 | 2022-01-19 11:50:44 | 2022-01-19 11:51:06 | 2022-01-19 11:51:57 | Chang Fook Keong Alan | The lock I have fixed back | [6 empty] | Medical fridge can't lock-Allan-low
FID6022 | Mechanical | Pneumatic Tube | Cannot Open or Close | Localised to room | RMG > RH > 2 > RM@RH |  | 2022-01-13 14:23:23 | 2022-01-13 14:23:42 | 2022-01-13 14:24:00 | 2022-01-13 14:24:18 | 2022-01-13 14:24:36 | 2022-01-13 14:25:27 | Muthu Shanmugavelu | fixed back and door working nornal | [6 empty] | Pneumatic tube station door came out-Shanmu-low
FID6017 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > CSSD |  | 2022-01-13 13:59:03 | 2022-01-27 14:44:25 | 2022-01-27 14:44:45 | 2022-01-27 14:45:10 | 2022-01-27 14:46:04 | 2022-01-27 14:46:46 | FRC | Informed to Getinge vendor to check. Rectified |  |  |  |  | 1 |  | Washer 2 got error-ilayaraja-low
FID6013 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Women Centre Consult Rm 2 |  | 2022-01-13 12:04:05 | 2022-01-13 12:22:11 | 2022-01-13 12:23:39 | 2022-01-13 12:24:48 | 2022-01-13 12:25:53 | 2022-01-13 12:27:15 | Sivalingam Ilayaraja | replaced the new light | [6 empty] | Light fused-ilayaraja-low
FID6012 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RSC > B2 > Female Toilet |  | 2022-01-13 11:56:14 | 2022-01-13 14:02:18 | 2022-01-13 14:02:39 | 2022-01-13 14:03:08 | 2022-01-13 14:03:27 | 2022-01-13 14:04:07 | Chang Fook Keong Alan | Power trip restart back | [6 empty] | No lights-Allan-low
FID6009 | Medical Equipment | CSSD Washers & WPT | Alarm | Localised to room | RMG > RH > 7 > CSSD |  | 2022-01-13 11:36:22 | 2022-01-13 11:36:44 | 2022-01-13 11:37:46 | 2022-01-13 11:38:04 | 2022-01-13 14:20:07 | 2022-01-13 19:52:57 | Muthu Shanmugavelu | Getinge updated one surgical equipment struck at door inside cause this fault..Now washer 2 back to normal.. | [6 empty] | Washer 2 got alarm-Shanmu-low
FID6007 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2022-01-13 11:15:56 | 2022-01-13 22:42:03 | 2022-01-13 22:42:37 | 2022-01-13 22:43:01 | 2022-01-13 22:43:28 | 2022-01-13 22:44:39 | Muthu Sathasivam | adjusted the setpoint tempe and deactivate heater | [6 empty] | Aircon make cool-satha-low
FID6006 | Mechanical | Air Diffuser (supply/return) | Airflow too strong / weak | Localised to room | RMG > RH > 2 > Healthcheck Consult Rm 6 |  | 2022-01-13 11:14:14 | 2022-01-13 22:45:29 | 2022-01-13 22:45:57 | 2022-01-13 22:46:09 | 2022-01-13 22:47:07 | 2022-01-13 22:48:25 | Muthu Sathasivam | adjusted the damper position | [6 empty] | Aircon air flow too strong-satha-low
FID6004 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > RHS Shanghai Rm |  | 2022-01-13 10:16:10 | 2022-01-13 14:04:47 | 2022-01-13 14:05:10 | 2022-01-13 14:05:30 | 2022-01-13 14:05:57 | 2022-01-13 14:06:34 | Chang Fook Keong Alan | Have replace a new bulb | [6 empty] | Light flickering-Allan-low
FID6000 | Plumbing & Sanitary | Hot Water System | Other: no hot water | Localised to room | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2022-01-13 09:57:10 | 2022-01-13 14:07:02 | 2022-01-13 14:07:22 | 2022-01-13 14:07:41 | 2022-01-13 14:08:05 | 2022-01-13 14:08:44 | Chang Fook Keong Alan | Hot water heater Back to normal | [6 empty] | Toilet no hot water-Allan-low
FID5999 | Building | Door Knob / Handle | Misaligned / dangling | Localised to room | RMG > RH > 3 > Biohazard Waste Rm |  | 2022-01-13 09:54:33 | 2022-01-13 10:01:01 | 2022-01-13 10:01:38 | 2022-01-13 10:04:50 | 2022-01-13 10:05:33 | 2022-01-13 10:07:04 | Sivalingam Ilayaraja | tightend the screw then normal back. | [6 empty] | Door handle spoilt-ilayaraja-low
FID5992 | Plumbing & Sanitary | Tap | Other: sensor no stop | Localised to room | RMG > RH > 7 > Operating Theatre 4 |  | 2022-01-13 08:07:50 | 2022-01-13 19:53:44 | 2022-01-13 19:54:09 | 2022-01-13 19:54:32 | 2022-01-13 19:54:51 | 2022-01-13 19:55:30 | Muthu Shanmugavelu | stop waterfowl and back to normal | [6 empty] | Water non-stop flushing-shanmu-low
FID5991 | Medical Equipment | Fridges & Freezers | Other: testo no battery | Localised to room | RMG > RH > 8 > Labour Ward Nursery |  | 2022-01-13 07:55:17 | 2022-01-27 14:42:12 | 2022-01-27 14:42:32 | 2022-01-27 14:42:51 | 2022-01-27 14:43:12 | 2022-01-27 14:43:45 | FRC | replaced new battery for testo data logger | [6 empty] | Testo data logger not working -aru-low
FID5990 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 10 > Ward 1022 |  | 2022-01-13 06:33:30 | 2022-01-27 14:39:46 | 2022-01-27 14:40:06 | 2022-01-27 14:40:37 | 2022-01-27 14:40:59 | 2022-01-27 14:41:25 | FRC | Cleared the choke | [6 empty] | Sink choke-aru-low
FID5989 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1048 |  | 2022-01-13 01:42:56 | 2022-01-27 14:35:36 | 2022-01-27 14:36:28 | 2022-01-27 14:36:49 | 2022-01-27 14:37:09 | 2022-01-27 14:37:43 | FRC | Adjusted the aircon temperature make it warm in bms system | [6 empty] | Aircon make it warm-aru-low
FID5988 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn C |  | 2022-01-13 01:39:03 | 2022-01-26 17:46:33 | 2022-01-26 17:47:42 | 2022-01-26 17:49:00 | 2022-01-26 17:49:23 | 2022-01-26 17:50:04 | FRC | Adjusted the temperature in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID5987 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Nursing Stn D |  | 2022-01-13 01:32:01 | 2022-01-26 17:34:11 | 2022-01-26 17:34:52 | 2022-01-26 17:35:41 | 2022-01-26 17:36:07 | 2022-01-26 17:37:17 | FRC | Adjusted the diffuser onsite to make cool | [6 empty] | Aircon make it cool-aru-low
FID5986 | Office and Furniture | Table | Other: table srew missing | Affecting Public | RMG > RH > 10 > Nursing Stn D |  | 2022-01-13 01:27:42 | 2022-01-26 17:28:57 | 2022-01-26 17:29:33 | 2022-01-26 17:30:15 | 2022-01-26 17:30:50 | 2022-01-26 17:31:37 | FRC | Fixed back the table screw | [6 empty] | Table screw missing-aru-low
FID5983 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 7 > ICU Counter A |  | 2022-01-13 00:03:48 | 2022-01-13 00:08:50 | 2022-01-13 00:09:13 | 2022-01-13 00:09:43 | 2022-01-13 00:10:04 | 2022-01-13 00:12:29 | Rajendran Manikandan | system problem power no coming | [6 empty] | door bell system not working-mani-low
FID5980 | Mechanical | Pneumatic Tube | Other: pnematic tube broken | Localised to room | RMG > RH > 2 > RM@RH Counter |  | 2022-01-12 23:02:07 | 2022-01-26 17:25:48 | 2022-01-26 17:26:11 | 2022-01-26 17:26:32 | 2022-01-26 17:26:53 | 2022-01-26 17:27:25 | FRC | Pneumatic tube broken. Temporary replaced with spare tube | [6 empty] | Need to the change pneumatic tube -aru-low
FID5979 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 922 |  | 2022-01-12 22:51:54 | 2022-01-13 00:05:12 | 2022-01-13 00:05:43 | 2022-01-13 00:06:06 | 2022-01-13 00:06:45 | 2022-01-13 00:08:28 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering -mani-low
FID5978 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-12 22:44:10 | 2022-01-26 17:17:01 | 2022-01-26 17:17:51 | 2022-01-26 17:18:18 | 2022-01-26 17:18:44 | 2022-01-26 17:20:07 | FRC | Adjusted the diffuser onsite to make it cool | [6 empty] | Aircon make it cool-aru-low
FID5975 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 703 |  | 2022-01-12 20:28:05 | 2022-01-12 20:29:36 | 2022-01-12 20:30:11 | 2022-01-12 20:30:38 | 2022-01-12 20:30:59 | 2022-01-12 20:33:09 | Vadivelu Balasubramanian | adjusted temperature in display setpoint make it cool | [6 empty] | Aircon too warm-v.bala-low
FID5973 | Plumbing & Sanitary | Tap | Water flowing non-stop | More than 1 room | RMG > RH > 11 > Level 11 |  | 2022-01-12 18:14:32 | 2022-01-12 20:06:06 | 2022-01-12 20:06:32 | 2022-01-12 20:07:02 | 2022-01-12 20:07:37 | 2022-01-12 20:08:54 | Vadivelu Balasubramanian | sensor clean back to normal |  |  |  |  | 1 |  | Basin tap sensor faulty-V.Bala-low
FID5972 | Plumbing & Sanitary | WC / Squatting Pedestal | Other: flush button not woking | More than 1 room | RMG > RH > 8 > Ward 850 |  | 2022-01-12 18:05:34 | 2022-01-19 12:38:00 | 2022-01-19 12:38:20 | 2022-01-19 12:38:41 | 2022-01-19 12:38:59 | 2022-01-19 12:40:35 | Hossain | onsite check & replaced the WC piston. flashing system back to normal. |  |  |  |  | 1 |  | Toilet flush not working-Hossain-low
FID5971 | Office and Furniture | Wall Clock | Other: battery need to replace | More than 1 room | RMG > RH > 9 > Ward 923 |  | 2022-01-12 16:55:52 | 2022-01-19 12:41:43 | 2022-01-19 12:42:04 | 2022-01-19 12:42:24 | 2022-01-19 12:42:32 | 2022-01-19 12:43:37 | Hossain | Replaced the wall clock battery. |  |  |  |  | 1 |  | Wall clock battery need to replace-Hossain-low
FID5966 | Medical Equipment | Medical Gas | Change Cylinders | More than 1 room | RMG > RSC > 9 > Internal Med |  | 2022-01-12 16:14:13 | 2022-01-12 20:10:03 | 2022-01-12 20:10:28 | 2022-01-12 20:10:38 | 2022-01-12 20:10:55 | 2022-01-12 20:11:53 | Vadivelu Balasubramanian | replaced new oxygen cylinder 1 |  |  |  |  | 1 |  | Need to replace one oxygen cylinder-V.Bala-medium
FID5965 | Electrical | Socket | Cracked / damaged | WIthin Building | RMG > RH > 10 > Ward 1017 |  | 2022-01-12 16:11:21 | 2022-01-12 20:12:45 | 2022-01-12 20:13:16 | 2022-01-12 20:13:43 | 2022-01-12 20:14:10 | 2022-01-12 20:15:38 | Vadivelu Balasubramanian | replaced socket |  |  |  |  | 1 |  | Plug socket broken-V.Bala-low
FID5963 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 8 > Ward 860-861 |  | 2022-01-12 15:18:55 | 2022-01-12 15:27:08 | 2022-01-12 15:28:15 | 2022-01-12 15:29:19 | 2022-01-12 15:29:50 | 2022-01-12 15:37:58 | Sivalingam Ilayaraja | cleared the choke. |  |  |  |  | 1 |  | Basin choke-ilayaraja-low
FID5962 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Ward 902 |  | 2022-01-12 15:08:53 | 2022-01-12 17:20:45 | 2022-01-12 17:21:05 | 2022-01-12 17:21:26 | 2022-01-12 17:21:45 | 2022-01-12 17:22:44 | Chang Fook Keong Alan | Have replace a new bulb |  |  |  |  | 1 |  | Light fused-Allan-low
FID5961 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 11 > Room 1128 (HR) |  | 2022-01-12 15:04:49 | 2022-01-12 17:23:18 | 2022-01-12 17:23:42 | 2022-01-12 17:24:02 | 2022-01-12 17:24:23 | 2022-01-12 17:25:37 | Chang Fook Keong Alan | Have change a new bulb |  |  |  |  | 1 |  | Light flickering-Allan-low
FID5960 | Building | Hand Rail | Other: hand rail drop | Affecting Public | RMG > RH > 10 > Ward 1019 |  | 2022-01-12 15:00:42 | 2022-01-19 12:46:09 | 2022-01-19 12:46:31 | 2022-01-19 12:46:43 | 2022-01-19 12:47:11 | 2022-01-19 12:49:34 | Hossain | onsite found bed Guard dropped. refixed back properly the bed guard back to normal. |  |  |  |  | 1 |  | Bed guard dropped-Hossain-low
FID5958 | Medical Equipment | Baby Cot | Other: screw loose | Affecting Public | RMG > RH > 8 > Delivery Suite 1 |  | 2022-01-12 14:56:00 | 2022-01-12 20:16:29 | 2022-01-12 20:16:57 | 2022-01-12 20:17:25 | 2022-01-12 20:18:00 | 2022-01-12 20:19:04 | Vadivelu Balasubramanian | screw tighten |  |  |  |  | 1 |  | Baby cot screw loose-v.bala-low
FID5956 | Building | Door Knob / Handle | Misaligned / dangling | Affecting Public | RMG > RH > 12 > RHS RM 18 |  | 2022-01-12 14:53:29 | 2022-01-12 15:42:45 | 2022-01-12 15:43:03 | 2022-01-12 15:43:21 | 2022-01-12 15:45:46 | 2022-01-12 15:46:48 | liumingcai | repaired |  |  |  |  | 1 |  | Door handle faulty-Ming cai-low
FID5954 | Plumbing & Sanitary | Soap Dispenser | Damaged / Loose / Cracked | Affecting Public | RMG > RSC > 8 > Children Centre |  | 2022-01-12 14:39:34 | 2022-01-19 12:50:33 | 2022-01-19 12:51:12 | 2022-01-19 12:51:33 | 2022-01-19 12:51:45 | 2022-01-19 12:55:03 | Hossain | refixed bcak the sop dispenser |  |  |  |  | 1 |  | Soap dispenser dropped-Hossain-low
FID5953 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RH > 2 > Healthcheck Consult Rm 6 |  | 2022-01-12 14:34:13 | 2022-01-19 12:56:47 | 2022-01-19 12:57:10 | 2022-01-19 12:57:24 | 2022-01-19 12:57:44 | 2022-01-19 13:00:57 | Hossain | onsite check & found door closer unable to adjust informed engineer Murogan he will arrange to replace the door closer. |  |  |  |  | 1 |  | Door cannot close-Hossain-low
FID5944 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 13 > Ward 1310-1318 |  | 2022-01-12 12:13:09 | 2022-01-12 12:48:40 | 2022-01-12 12:49:47 | 2022-01-12 12:50:57 | 2022-01-12 12:52:08 | 2022-01-12 12:54:01 | Sivalingam Ilayaraja | cleared the chock | [6 empty] | Basin choke-ilayaraja-low
FID5939 | Building | Wall | Paint peeling / stained | Affecting Public | RMG > RSC > 13 > Link Bridge |  | 2022-01-12 11:16:44 | 2022-01-12 11:20:12 | 2022-01-12 11:40:28 | 2022-01-12 13:35:23 | 2022-01-12 13:36:13 | 2022-01-12 13:37:29 | Sivalingam Ilayaraja | glue back | [6 empty] | Wall paper come off-ilayaraja-low
FID5937 | Plumbing & Sanitary | Hot Water System | No water | Localised to room | RMG > RH > 8 > Ward 842 (Ophir Suite) |  | 2022-01-12 11:08:21 | 2022-01-12 11:10:06 | 2022-01-12 13:38:56 | 2022-01-12 13:40:03 | 2022-01-12 13:41:52 | 2022-01-12 13:43:30 | Sivalingam Ilayaraja | hot water valve on back | [6 empty] | No hot water-ilayaraja-low
FID5935 | Plumbing & Sanitary | Urinal | Choked | Affecting Public | RMG > RSC > 9 > Male Toilet |  | 2022-01-12 11:03:30 | 2022-01-12 11:07:50 | 2022-01-12 11:11:50 | 2022-01-12 13:44:55 | 2022-01-12 13:47:27 | 2022-01-12 13:50:12 | Sivalingam Ilayaraja | cleared the chock | [6 empty] | Urinal choke-ilayaraja-low
FID5934 | Building | Pipe | Leaking | Localised to room | RMG > RSC > 11 > Radiology |  | 2022-01-12 10:59:45 | 2022-01-12 12:16:22 | 2022-01-12 12:17:19 | 2022-01-12 12:17:43 | 2022-01-12 12:18:32 | 2022-01-12 12:37:18 | Hossain | onsite found bidet spray hose spoiled. Replaced the bidet spray hose back to normal. | [6 empty] | Toilet bidet spray hose leaking-hossain-low
FID5933 | Office and Furniture | TV | Cannot operate / defective | Affecting Public | RMG > RSC > 13 > Surgical Ctr Waiting |  | 2022-01-12 10:50:56 | 2022-01-19 11:56:08 | 2022-01-19 11:56:26 | 2022-01-19 11:56:44 | 2022-01-19 11:57:04 | 2022-01-19 11:57:43 | Chang Fook Keong Alan | Reset back the Tv back to normal | [6 empty] | TV not working-Allan-low
FID5931 | Mechanical | Hot and Cold Water Dispenser | Cannot Open or Close | Affecting Public | RMG > RSC > 11 > Radiology Counter |  | 2022-01-12 10:41:32 | 2022-01-12 11:20:06 | 2022-01-12 11:20:40 | 2022-01-12 11:20:53 | 2022-01-12 11:21:06 | 2022-01-12 11:22:07 | Muthu Sathasivam | replace new water tap | [6 empty] | Water dispenser hot tap broken-satha-low
FID5903 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Nursing Stn B |  | 2022-01-11 21:47:03 | 2022-01-26 17:14:06 | 2022-01-26 17:14:26 | 2022-01-26 17:14:48 | 2022-01-26 17:15:10 | 2022-01-26 17:15:44 | FRC | Open the diffuser onsite to make it cool | [6 empty] | Aircon make cool-aru-low
FID5896 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > Dental Surgery 8 |  | 2022-01-11 18:16:24 | 2022-01-12 09:15:54 | 2022-01-12 09:16:24 | 2022-01-12 09:16:42 | 2022-01-12 09:17:51 | 2022-01-15 11:16:03 | Li Fei | Purchased new led panal and replaced |  |  |  |  | 2 |  | Light fused-mani-low
FID5893 | Medical Equipment | Medical Gas | Leaking | Affecting Public | RMG > RH > 8 > NICU |  | 2022-01-11 16:02:22 | 2022-01-12 11:42:45 | 2022-01-12 11:43:19 | 2022-01-12 11:43:49 | 2022-01-12 11:44:19 | 2022-01-26 17:13:08 | FRC | Arranged the contractor to replace the oxygen terminal. Completed |  |  |  |  | 1 |  | Oxygen port leaking-V.Bala-medium
FID5892 | Building | Door Knob / Handle | Other: door handle loose | Affecting Public | RMG > RSC > 9 > Neuroscience Ctr Counter |  | 2022-01-11 15:49:12 | 2022-01-11 17:00:54 | 2022-01-11 17:01:14 | 2022-01-11 17:01:36 | 2022-01-11 17:02:00 | 2022-01-11 17:02:37 | Chang Fook Keong Alan | I have tied back to handle |  |  |  |  | 1 |  | Door handle loose-Allan-low
FID5891 | Plumbing & Sanitary | Water Heater | No water | Affecting Public | RMG > RH > 10 > Ward 1041 |  | 2022-01-11 15:35:34 | 2022-01-12 09:27:39 | 2022-01-12 09:28:09 | 2022-01-12 09:28:34 | 2022-01-12 09:29:03 | 2022-01-12 09:32:37 | Vadivelu Balasubramanian | hot water not coming due to shower handle didn't open properly |  |  |  |  | 1 |  | No hot water-V.Bala-low
FID5889 | Plumbing & Sanitary | WC / Squatting Pedestal | Choked | Affecting Public | RMG > RSC > 1 > Male Toilet |  | 2022-01-11 15:04:08 | 2022-01-12 09:50:56 | 2022-01-12 09:51:26 | 2022-01-12 09:52:01 | 2022-01-12 11:45:23 | 2022-01-12 11:46:43 | Vadivelu Balasubramanian | bowl choke cleared |  |  |  |  | 1 |  | Toilet bowl choke-V.Bala-low
FID5888 | Building | Door Closer | Noisy | Affecting Public | RMG > RH > 7 > Dialysis Centre |  | 2022-01-11 14:59:19 | 2022-01-12 12:39:05 | 2022-01-12 12:39:46 | 2022-01-12 12:41:01 | 2022-01-19 13:04:06 | 2022-01-19 13:08:22 | Hossain | onsite check & rectified the door issue back to normal. |  |  |  |  | 1 |  | Door noisy-hossain-low
FID5885 | Plumbing & Sanitary | Water Tank | No water | WIthin Building | RMG > RH > Rooftop > Water Tank Place |  | 2022-01-11 13:40:39 | 2022-01-11 13:40:58 | 2022-01-11 13:41:15 | 2022-01-11 13:41:33 | 2022-01-11 13:41:46 | 2022-01-11 16:14:49 | Muthu Shanmugavelu | washing completed by waves fluid contractor | [6 empty] | waves fluid contractor washing RH L15 tank 1B compartment-Escort-Shanmu-low
FID5884 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Ward 8 |  | 2022-01-11 12:43:05 | 2022-01-12 11:48:03 | 2022-01-12 11:48:40 | 2022-01-12 11:49:13 | 2022-01-12 11:49:44 | 2022-01-12 11:51:52 | Vadivelu Balasubramanian | adjusted temperature in bms setpoint 17to15 reduce aircon make it cool | [6 empty] | Aircon make it cool-v.bala-low
FID5882 | Plumbing & Sanitary | Basin / sink | Damaged / Loose / Cracked | Localised to room | RMG > RH > 7 > Cytology Lab |  | 2022-01-11 12:33:09 | 2022-01-12 11:52:58 | 2022-01-12 11:53:19 | 2022-01-12 11:54:05 | 2022-01-12 11:54:37 | 2022-01-12 11:57:49 | Vadivelu Balasubramanian | basin water tap open continue after dirty water change normal | [6 empty] | Water tap water dirty-v.bala-low
FID5880 | Plumbing & Sanitary | Basin / sink | Water flowing non-stop | Localised to room | RMG > RH > 12 > RHS Female Toilet |  | 2022-01-11 11:59:49 | 2022-01-11 14:28:56 | 2022-01-11 14:29:16 | 2022-01-11 14:29:35 | 2022-01-11 14:29:56 | 2022-01-11 14:30:47 | Chang Fook Keong Alan | I have check the water is clean now | [6 empty] | Basin water tap water dirty-allan-low
FID5875 | Mechanical | Pneumatic Tube | System Shows fault / Error code | WIthin Building | RMG > RH > 12 > Women Centre |  | 2022-01-11 11:15:03 | 2022-01-11 11:15:33 | 2022-01-11 11:16:05 | 2022-01-11 11:16:22 | 2022-01-11 11:16:31 | 2022-01-12 09:24:18 | Muthu Shanmugavelu | Mecomb replaced card and PTS back to normal.. | [6 empty] | Pnematic tube system card faulty-shanmu-low
FID5874 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 7 > ICU |  | 2022-01-11 11:03:31 | 2022-01-11 11:06:23 | 2022-01-11 11:07:04 | 2022-01-11 11:07:30 | 2022-01-11 11:07:53 | 2022-01-11 11:09:41 | Muthu Shanmugavelu | reset back to normal,tightened wiring.. | [6 empty] | Medical gas zone wall unit alarming faulty-shanmu-medium
FID5873 | Medical Equipment | Fridges & Freezers | Leaking | Localised to room | RMG > RH > 2 > Skin & Aesthetics Treatment Rm 7 |  | 2022-01-11 10:58:53 | 2022-01-11 11:04:38 | 2022-01-11 11:05:02 | 2022-01-11 11:05:33 | 2022-01-19 13:09:21 | 2022-01-19 15:28:37 | Hossain | onside check with user she want to dispose the fridge due to spoiled. Brought the fridge from there & keep at L6 store. | [6 empty] | Fridge spoil-Hossain-low
FID5870 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-11 10:07:39 | 2022-01-11 10:08:21 | 2022-01-11 10:08:39 | 2022-01-11 10:08:56 | 2022-01-11 10:09:17 | 2022-01-11 10:15:39 | Muthu Shanmugavelu | replaced empty cylinders with full | [6 empty] | N2 change cylinder alarming-Shanmu-medium
FID5868 | Plumbing & Sanitary | Water Tank | No water | WIthin Building | RMG > RH > 4 > Transfer Water Tank Rm |  | 2022-01-11 09:47:42 | 2022-01-11 09:48:12 | 2022-01-11 09:48:29 | 2022-01-11 09:48:46 | 2022-01-11 09:49:05 | 2022-01-11 11:42:55 | Muthu Shanmugavelu | washing completed by the contractor. | [6 empty] | Escort contractor washing water tank at L4 1 compartment-Shanmu-low
FID5824 | Mechanical | Air Diffuser (supply/return) | Airflow too strong / weak | Localised to room | RMG > RH > 9 > Ward 922 |  | 2022-01-10 22:38:58 | 2022-01-10 22:44:25 | 2022-01-10 22:44:54 | 2022-01-10 22:46:35 | 2022-01-10 22:47:04 | 2022-01-10 22:48:34 | Muthu Sathasivam | system working normally but still people complain very warm adjusted the damper manually to 100 % | [6 empty] | Aircon make cool-satha-low
FID5823 | Mechanical | Pneumatic Tube | Noisy | Whole Building | RMG > RH > 13 > Ward 13 Nurse Counter |  | 2022-01-10 22:37:22 | 2022-01-10 22:43:38 | 2022-01-10 22:44:15 | 2022-01-10 22:49:41 | 2022-01-10 22:51:36 | 2022-01-10 22:55:48 | Muthu Sathasivam | card faulty level 13 and 12 also cannot use all other level can use | [6 empty] | Pneumatic system faulty-satha-low
FID5818 | Building | Door Lock | Other: no working | Whole Building | RMG > RSC > 16 > Eye Centre |  | 2022-01-10 19:58:11 | 2022-01-26 16:09:34 | 2022-01-26 16:14:47 | 2022-01-26 16:15:14 | 2022-01-26 16:15:36 | 2022-01-26 16:16:19 | FRC | Adjusted the glass door lock and opened | [6 empty] | Glass door can't open-aru-low
FID5817 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1029 |  | 2022-01-10 19:47:52 | 2022-01-26 16:04:45 | 2022-01-26 16:05:08 | 2022-01-26 16:05:35 | 2022-01-26 16:05:56 | 2022-01-26 16:06:59 | FRC | Adjusted the room vav damper position in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID5816 | Plumbing & Sanitary | Flush Button | No water | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2022-01-10 19:46:23 | 2022-01-11 13:38:44 | 2022-01-26 16:02:32 | 2022-01-26 16:02:53 | 2022-01-26 16:03:22 | 2022-01-26 16:03:57 | FRC | Repaired the toilet flushing system | [6 empty] | Toilet flush water not coming out-aru-low
FID5815 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1031 |  | 2022-01-10 19:41:23 | 2022-01-26 15:20:18 | 2022-01-26 15:20:43 | 2022-01-26 15:21:04 | 2022-01-26 15:27:25 | 2022-01-26 15:28:10 | FRC | Adjusted the room vav damper position in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID5814 | Plumbing & Sanitary | Flush Button | No water | Localised to room | RMG > RH > 10 > Ward 1019 |  | 2022-01-10 19:39:27 | 2022-01-19 11:59:12 | 2022-01-19 11:59:44 | 2022-01-19 12:00:04 | 2022-01-19 12:00:44 | 2022-01-19 12:01:24 | Chang Fook Keong Alan | Have reset back to normal | [6 empty] | Toilet flush no water-allan-low
FID5813 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn D |  | 2022-01-10 19:33:29 | 2022-01-26 15:16:19 | 2022-01-26 15:17:21 | 2022-01-26 15:17:42 | 2022-01-26 15:18:02 | 2022-01-26 15:18:45 | FRC | Adjusted the vav temperature setpoint and damper position make it cool in bms system | [6 empty] | Aircon make it cool-aru-low
FID5805 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RSC > 10 > Heart Ctr Procedure Rm 5 |  | 2022-01-10 14:50:12 | 2022-01-26 15:11:38 | 2022-01-26 15:12:24 | 2022-01-26 15:13:59 | 2022-01-26 15:14:36 | 2022-01-26 15:15:44 | FRC | Adjusted the room vav aircon temperature setpoint make it cool in bms system | [6 empty] | Aircon make it cool-aru-low
FID5804 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-10 14:47:51 | 2022-01-26 15:08:37 | 2022-01-26 15:08:59 | 2022-01-26 15:09:27 | 2022-01-26 15:09:51 | 2022-01-26 15:10:46 | FRC | Adjusted the aircon temperature in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID5801 | Medical Equipment | Medical Gas | Alarm | Localised to room | RMG > RH > 7 > OT |  | 2022-01-10 14:38:58 | 2022-01-10 14:46:21 | 2022-01-10 14:46:40 | 2022-01-10 14:47:33 | 2022-01-10 14:47:51 | 2022-01-10 15:01:54 | Muthu Shanmugavelu | calibration done by Ansac | [6 empty] | Nitric oxide gas meter calibration by Ansac-Shanmu-low
FID5800 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Level 7 |  | 2022-01-10 14:28:46 | 2022-01-10 16:49:19 | 2022-01-10 16:49:46 | 2022-01-10 16:50:08 | 2022-01-10 16:50:30 | 2022-01-10 16:51:09 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light fused-mani-low
FID5799 | Medical Equipment | Patient Bed | Other: no working | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2022-01-10 14:26:59 | 2022-01-11 09:59:06 | 2022-01-11 09:59:28 | 2022-01-11 09:59:49 | 2022-01-12 09:14:31 | 2022-01-12 09:15:00 | liumingcai | repair | [6 empty] | Bed not working-Hossain-low
FID5798 | Electrical | Lightning Protection System | Flickering / Blown | Localised to room | RMG > RH > 7 > Lab Office |  | 2022-01-10 14:07:40 | 2022-01-11 14:38:20 | 2022-01-11 14:39:17 | 2022-01-11 14:41:32 | 2022-01-11 14:42:37 | 2022-01-11 14:43:48 | Arasan Balasubramanian | replaced new light bulb |  |  |  |  | 2 |  | Two light flickering-a.bala-low
FID5797 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 11 > Inpatient Pharmacy |  | 2022-01-10 13:58:41 | 2022-01-26 15:05:34 | 2022-01-26 15:06:09 | 2022-01-26 15:06:31 | 2022-01-26 15:06:54 | 2022-01-26 15:07:40 | FRC | Manually close the damper slightly onsite to make the aircon warm |  |  |  |  | 2 |  | Aircon make it warm-aru-low
FID5795 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn B |  | 2022-01-10 13:40:11 | 2022-01-26 15:02:32 | 2022-01-26 15:02:53 | 2022-01-26 15:03:12 | 2022-01-26 15:03:33 | 2022-01-26 15:04:09 | FRC | Adjusted the aircon temperature in bms system make it cool | [6 empty] | Aircon make it cool-aru-low
FID5794 | Office and Furniture | TV | Other: temporary swop | Localised to room | RMG > RH > 10 > Ward 1009 |  | 2022-01-10 13:17:59 | 2022-01-26 14:23:10 | 2022-01-26 14:24:11 | 2022-01-26 14:24:37 | 2022-01-26 14:24:58 | 2022-01-26 14:27:14 | FRC | Remove the TV as per requested | [6 empty] | Need to remove 1001, 1009, and 1045 TV-a.bala-low
FID5790 | Plumbing & Sanitary | Water Tank | No water | Whole Building | RMG > RSC > Roof > Water Tank Space |  | 2022-01-10 12:11:01 | 2022-01-10 12:11:44 | 2022-01-10 12:12:02 | 2022-01-10 12:12:21 | 2022-01-10 12:12:39 | 2022-01-10 16:33:25 | Muthu Shanmugavelu | Rsc RT water tank washing completed by waves fluid contractor. | [6 empty] | waves fluid contractor washing water tank compartment 1B at L23- Shanmu-low
FID5781 | Plumbing & Sanitary | Water Tank | No water | Whole Building | RMG > RSC > 5 > Domestic Water Transfer Tank Place |  | 2022-01-10 09:52:43 | 2022-01-10 09:53:07 | 2022-01-10 09:53:25 | 2022-01-10 09:53:45 | 2022-01-10 09:54:03 | 2022-01-10 12:04:46 | Muthu Shanmugavelu | cleaning completed | [6 empty] | Water tank washing for L5 1B compartment-Shanmu-low
FID5774 | Medical Equipment | Medical Gas | Change Cylinders | More than 1 room | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-10 08:39:58 | 2022-01-10 08:40:20 | 2022-01-10 08:40:48 | 2022-01-10 08:41:24 | 2022-01-10 08:47:46 | 2022-01-10 08:48:20 | Muthu Shanmugavelu | replaced 1 N2 cylinder | [6 empty] | N2 change cylinder alarming-Shanmu-medium
FID5773 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > A&E Critical Care Counter |  | 2022-01-10 08:39:53 | 2022-01-11 14:45:54 | 2022-01-11 14:47:10 | 2022-01-11 14:48:11 | 2022-01-11 14:49:10 | 2022-01-11 14:51:44 | Arasan Balasubramanian | replaced new light bulb | [6 empty] | Need to check the light-A.bala-low
FID5772 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Operating Theatre 11 |  | 2022-01-10 08:37:15 | 2022-01-26 14:16:33 | 2022-01-26 14:17:08 | 2022-01-26 14:17:54 | 2022-01-26 14:18:18 | 2022-01-26 14:18:49 | FRC | Replaced new light | [6 empty] | Need to change the light-A.bala-low
FID5765 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1007 |  | 2022-01-10 01:52:36 | 2022-01-10 01:54:02 | 2022-01-10 01:55:51 | 2022-01-10 01:56:15 | 2022-01-10 01:56:35 | 2022-01-10 01:57:30 | Muthu Sathasivam | adjusted the damper position already put 5% manually and put back to auto 90% | [6 empty] | Aircon make cool-satha-low
FID5748 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-09 03:47:07 | 2022-01-09 08:08:08 | 2022-01-09 08:08:32 | 2022-01-09 08:08:57 | 2022-01-09 08:09:22 | 2022-01-09 08:10:25 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 20to24 make it warm | [6 empty] | Aircon make it warm-V.Bala-low
FID5738 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Operating Theatre 5 |  | 2022-01-08 15:37:12 | 2022-01-09 09:53:54 | 2022-01-09 09:54:22 | 2022-01-09 09:54:47 | 2022-01-09 09:55:18 | 2022-01-09 09:56:59 | Rajendran Manikandan | auto door switch on and normal back | [6 empty] | No power-mani-high
FID5733 | Mechanical | Air Handling Unit | Too hot / Too cold | More than 1 room | RMG > RSC > B2 > B2 |  | 2022-01-08 13:51:50 | 2022-01-08 13:52:34 | 2022-01-08 13:53:18 | 2022-01-08 13:54:11 | 2022-01-08 13:54:36 | 2022-01-08 13:55:16 | Muthu Sathasivam | on the ahu as per user request | [6 empty] | Request to on ahu until 5 pm-satha-low
FID5732 | Mechanical | Air Handling Unit | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 10 |  | 2022-01-08 13:46:06 | 2022-01-08 13:48:36 | 2022-01-08 13:49:04 | 2022-01-08 13:49:33 | 2022-01-08 13:50:00 | 2022-01-08 13:50:48 | Muthu Sathasivam | adjusted setpoint to 18 degrees and deactivate heater | [6 empty] | Aircon make cool-satha-low
FID5731 | Electrical | Socket | Tripped / Short-Circuit / Overloaded | More than 1 room | RMG > RSC > 8 > Counselling Ctr Counter |  | 2022-01-08 13:43:09 | 2022-01-08 14:15:06 | 2022-01-08 14:15:43 | 2022-01-08 14:16:20 | 2022-01-08 14:16:50 | 2022-01-08 14:18:14 | Rajendran Manikandan | Rccb reset normal back | [6 empty] | Power trip, PC not working-mani-high
FID5724 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1025 |  | 2022-01-08 10:54:10 | 2022-01-08 13:44:23 | 2022-01-08 13:45:11 | 2022-01-08 13:45:33 | 2022-01-08 13:46:09 | 2022-01-08 13:46:49 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Aircon make it warm-satha-low
FID5723 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RH > 13 > Male Toilet (Waiting Area) |  | 2022-01-08 10:53:09 | 2022-01-19 15:31:00 | 2022-01-19 15:31:21 | 2022-01-19 15:31:44 | 2022-01-19 15:32:02 | 2022-01-19 15:35:06 | Hossain | onsite check & found floor tap chocked unable to clear informed sudieana she arranged contractor to rectified this issue. | [6 empty] | Floor trap choke-Hossain, ilayarja-low
FID5722 | Office and Furniture | Cabinet | Other: Lock spoilt | Affecting Public | RMG > RSC > 11 > Radiology |  | 2022-01-08 10:52:24 | 2022-01-19 15:36:04 | 2022-01-19 15:36:46 | 2022-01-19 15:37:07 | 2022-01-19 15:37:42 | 2022-01-19 15:47:56 | Hossain | Onsite check & found cabinet lock key broken. Replaced the lock set back to normal. | [6 empty] | Staff locker lock broken-Hossain-low
FID5721 | Building | Ceiling | Leaking | Affecting Public | RMG > RH > 12 > Women Centre Consult Rm 7 |  | 2022-01-08 10:51:34 | 2022-01-19 15:48:44 | 2022-01-19 15:49:04 | 2022-01-19 15:49:22 | 2022-01-19 15:49:33 | 2022-01-19 15:55:06 | Hossain | onsite check & found room 7 water dripping from ceiling floor tap due to chocked. cleared the choked back to normal. | [6 empty] | Water leaking from ceiling-Hossain-low
FID5716 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-08 08:09:21 | 2022-01-09 08:12:03 | 2022-01-09 08:12:29 | 2022-01-09 08:12:52 | 2022-01-09 08:13:17 | 2022-01-09 08:14:50 | Vadivelu Balasubramanian | replaced 1 oxygen cylinder |  |  |  |  | 1 |  | Need to replace 1 small oxygen cylinder-v.bala-medium
FID5714 | Plumbing & Sanitary | Flush Button | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 7 > OT Female Changing Rm, RMG > RH |  | 2022-01-08 07:41:34 | 2022-01-09 08:15:30 | 2022-01-09 08:15:56 | 2022-01-09 08:16:22 | 2022-01-09 08:16:49 | 2022-01-09 08:17:53 | Vadivelu Balasubramanian | flushing system screw adjusted normal |  |  |  |  | 1 |  | Toilet flush not working-v.bala-low
FID5686 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 8 |  | 2022-01-07 19:05:59 | 2022-01-07 19:07:03 | 2022-01-07 19:07:37 | 2022-01-07 19:08:21 | 2022-01-07 19:12:31 | 2022-01-26 14:12:23 | FRC | adjusted the temperature to 28 degree and increase heater to 100% | [6 empty] | Aircon make warm-ilayaraja-low
FID5683 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1052 |  | 2022-01-07 18:54:45 | 2022-01-07 19:05:09 | 2022-01-07 19:05:42 | 2022-01-07 19:06:15 | 2022-01-07 19:09:19 | 2022-01-07 19:10:48 | Muthu Sathasivam | adjusted the setpoint temperaturea | [6 empty] | Aircon make warm-satha-low
FID5681 | Building | Wall Skirting | Misaligned / dangling | Localised to room | RMG > RH > 7 > ICU Rm 705 |  | 2022-01-07 18:19:14 | 2022-01-07 18:21:00 | 2022-01-07 18:21:51 | 2022-01-07 18:22:30 | 2022-01-07 18:23:04 | 2022-01-07 18:25:07 | Muthu Sathasivam | blind rotated in opposite directions return back to original direction and working fine | [6 empty] | Window blind spoilt-satha-low
FID5680 | Office and Furniture | Telephone | No dial tone / not connected | Localised to room | RMG > RH > 9 > Nursing Stn A |  | 2022-01-07 18:17:03 | 2022-01-07 18:19:44 | 2022-01-07 18:20:43 | 2022-01-07 18:21:14 | 2022-01-07 18:21:29 | 2022-01-07 18:21:55 | Muthu Shanmugavelu | reset back to normal.. | [6 empty] | IP telephone not working-Shanmu-low
FID5679 | Office and Furniture | TV | Cannot operate / defective | Localised to room | RMG > RH > 9 > Ward 969 - 970 |  | 2022-01-07 17:30:10 | 2022-01-07 17:40:05 | 2022-01-07 17:40:27 | 2022-01-07 17:40:39 | 2022-01-07 17:40:56 | 2022-01-07 17:41:36 | Muthu Shanmugavelu | Tv faulty..Temperorily swapped form 972 to 970... | [6 empty] | TV not working-Shanmu-low
FID5677 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 3 > Medical Gas Manifold Rm |  | 2022-01-07 16:36:38 | 2022-01-07 16:37:07 | 2022-01-07 16:37:39 | 2022-01-07 16:38:09 | 2022-01-07 16:38:39 | 2022-01-07 16:55:07 | Muthu Shanmugavelu | Replaced 2 N20 cylinders at reserve Bank... | [6 empty] | N2O reserve Bank cylinders expired-Shanmu-medium
FID5676 | Building | Door Frame | Noisy | Localised to room | RMG > RH > 8 > Labour Ward Nursery |  | 2022-01-07 16:30:42 | 2022-01-07 20:01:12 | 2022-01-07 20:01:43 | 2022-01-07 20:02:12 | 2022-01-07 20:02:48 | 2022-01-07 20:04:19 | Sivalingam Ilayaraja | replaced the new door closer | [6 empty] | Door noisy and oil spilled-ilayaraja-low
FID5675 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > Women Centre Consult Rm 17 |  | 2022-01-07 16:27:53 | 2022-01-07 16:28:22 | 2022-01-26 12:04:51 | 2022-01-26 12:05:09 | 2022-01-26 12:05:29 | 2022-01-26 12:05:52 | FRC | Replaced new light | [6 empty] | Light flickering-satha-low
FID5674 | Medical Equipment | Medical Gas | Change Cylinders | WIthin Building | RMG > RH > 1 > O2 Manifold RM |  | 2022-01-07 16:27:12 | 2022-01-07 16:27:43 | 2022-01-07 16:27:58 | 2022-01-07 16:28:47 | 2022-01-07 16:29:13 | 2022-01-07 16:30:07 | Muthu Shanmugavelu | replaced 4 nps O2 cylinders in duty bank..system normal | [6 empty] | Oxygen cylinder change alarming-Shanmu-medium
FID5673 | Building | Door Frame | Misaligned / dangling | Localised to room | RMG > RSC > 16 > Pantry |  | 2022-01-07 16:04:57 | 2022-01-07 20:05:59 | 2022-01-07 20:06:23 | 2022-01-07 20:06:56 | 2022-01-07 20:07:23 | 2022-01-07 20:08:51 | Sivalingam Ilayaraja | adjested the screw then normal back the door prame | [6 empty] | Door misaligned-ilayaraja-low
FID5672 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-07 16:01:15 | 2022-01-07 16:01:49 | 2022-01-07 16:08:12 | 2022-01-07 16:08:41 | 2022-01-07 16:09:14 | 2022-01-07 16:10:33 | Muthu Sathasivam | adjusted heater from 100 to 50 % | [6 empty] | Aircon make slightly cool-satha-low
FID5671 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 11 > Room 1126 (HR) |  | 2022-01-07 15:59:38 | 2022-01-07 16:00:58 | 2022-01-07 16:11:11 | 2022-01-07 16:11:35 | 2022-01-07 16:12:11 | 2022-01-07 16:13:09 | Muthu Sathasivam | open the damper to 100% check airflow about 2.26 | [6 empty] | Aircon very warm-satha-low
FID5670 | Office and Furniture | TV | Other: remote not working | Localised to room | RMG > RH > 10 > Ward 1053 |  | 2022-01-07 15:56:00 | 2022-01-07 16:03:29 | 2022-01-07 16:05:09 | 2022-01-07 16:06:00 | 2022-01-07 16:06:47 | 2022-01-07 16:07:26 | Muthu Sathasivam | battery spoiled replace new battery | [6 empty] | TV remote not working-satha-low
FID5667 | Building | Hand Rail | Chipped / Cracked | Localised to room | RMG > RH > 7 > OT |  | 2022-01-07 14:53:24 | 2022-01-07 16:21:46 | 2022-01-07 16:22:10 | 2022-01-07 16:22:48 | 2022-01-07 16:23:38 | 2022-01-07 16:26:24 | Hossain | onsite check & found wall Guard came off. fixed back properly the wall guard back to normal. | [6 empty] | Need to close the sharp edge-hossain-low
FID5664 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 2 > RJC Treatment Rm 7 |  | 2022-01-07 14:45:31 | 2022-01-19 12:05:13 | 2022-01-19 12:05:33 | 2022-01-19 12:06:08 | 2022-01-19 12:06:27 | 2022-01-19 12:07:22 | Chang Fook Keong Alan | Have change a new bulb | [6 empty] | Light fused-Allan-low
FID5663 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 2 > Healthcheck Handicap Toilet |  | 2022-01-07 14:25:49 | 2022-01-07 14:40:39 | 2022-01-07 14:41:04 | 2022-01-07 14:41:29 | 2022-01-07 14:51:51 | 2022-01-07 14:57:28 | Sivalingam Ilayaraja | cleared the choke | [6 empty] | Hand basin choke-ilayaraja-low
FID5658 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Counter A |  | 2022-01-07 14:01:02 | 2022-01-07 14:01:40 | 2022-01-07 14:02:17 | 2022-01-07 14:02:40 | 2022-01-07 14:03:16 | 2022-01-07 14:04:14 | Muthu Sathasivam | adjusted setpoint from 18 to 19 degree | [6 empty] | Aircon make warm-satha-low
FID5657 | Electrical | Call System | Other: no working | Localised to room | RMG > RH > 7 > ICU Rm 705 |  | 2022-01-07 13:59:31 | 2022-01-07 14:03:05 | 2022-01-07 14:03:29 | 2022-01-07 14:03:51 | 2022-01-07 14:04:15 | 2022-01-07 14:05:22 | Muthu Shanmugavelu | Room 705 call Bell now working normal..user f/b it not responding some times.. | [6 empty] | Call bell not working-Shanmu-low
FID5654 | Medical Equipment | CSSD Sterilisers | Alarm | More than 1 room | RMG > RH > 7 > CSSD |  | 2022-01-07 13:49:11 | 2022-01-07 13:49:42 | 2022-01-07 13:49:59 | 2022-01-07 13:50:20 | 2022-01-07 13:51:40 | 2022-01-07 18:34:09 | FRC | Getinge tech adjusted the calibration of sterliser 3,back to normal. | [6 empty] | Sterliser 3 continuously running rapid process-shanmu-low
FID5649 | Mechanical | Air Handling Unit | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-07 12:39:54 | 2022-01-07 12:40:52 | 2022-01-07 16:14:15 | 2022-01-07 16:14:31 | 2022-01-07 16:14:47 | 2022-01-07 16:18:58 | Hossain | adjusted the heater to 100% | [6 empty] | Aircon very cool, make it warm-satha-low
FID5648 | Building | Pipe | Leaking | Localised to room | RMG > RH > 7 > Operating Theatre 3 (Embryo Lab) |  | 2022-01-07 12:37:47 | 2022-01-26 12:01:50 | 2022-01-26 12:02:12 | 2022-01-26 12:02:33 | 2022-01-26 12:02:53 | 2022-01-26 12:04:05 | FRC | Checked and found water leaking from the water pipe above the ceiling. Temporary put clip for the water pipe to stop the water leaking | [6 empty] | Water leaking from ceiling-ming cai-medium
FID5647 | Electrical | Socket | Other: wire come out | Localised to room | RMG > RSC > 10 > Heart Ctr Counter |  | 2022-01-07 12:34:30 | 2022-01-26 11:38:54 | 2022-01-26 11:39:44 | 2022-01-26 11:40:04 | 2022-01-26 11:40:24 | 2022-01-26 11:40:53 | FRC | Tape back the wire | [6 empty] | Wire come out need to tape-ilayaraja-low
FID5646 | Mechanical | Air Diffuser (supply/return) | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2022-01-07 12:27:17 | 2022-01-07 12:27:59 | 2022-01-07 12:28:42 | 2022-01-07 12:29:14 | 2022-01-07 12:29:52 | 2022-01-07 12:30:38 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Aircon make cool-satha-low
FID5645 | Medical Equipment | Patient Bed | Other: cannot seat up | Localised to room | RMG > RH > 10 > Ward 1030 |  | 2022-01-07 12:23:51 | 2022-01-07 16:33:13 | 2022-01-07 16:33:34 | 2022-01-07 16:34:06 | 2022-01-07 16:34:54 | 2022-01-07 16:44:03 | Hossain | onside check & found patient bed was Lock mode. so that’s way unable to operate the bed. Unlock the patient bed mode back to normal. | [6 empty] | Bed cannot adjust up-hossain-low
FID5644 | Electrical | Call System | Other: need to change timing in call system | More than 1 room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-07 12:17:15 | 2022-01-07 12:21:17 | 2022-01-07 12:21:51 | 2022-01-07 12:22:11 | 2022-01-07 12:22:27 | 2022-01-07 12:24:19 | Muthu Sathasivam | replace tap | [6 empty] | Digital timing need to change-hossain-low
FID5643 | Medical Equipment | Medical Gas | Other: delivery | Localised to room | RMG > RH > 1 > VIE Tank Rm |  | 2022-01-07 12:14:59 | 2022-01-07 12:26:10 | 2022-01-07 12:31:20 | 2022-01-07 12:32:31 | 2022-01-08 09:53:57 | 2022-01-08 09:54:35 | Muthu Sathasivam | contractor delivery oxygen | [6 empty] | Delivery oxygen-satha-low
FID5642 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2022-01-07 12:11:01 | 2022-01-26 11:18:59 | 2022-01-26 11:19:18 | 2022-01-26 11:19:38 | 2022-01-26 11:20:03 | 2022-01-26 11:20:32 | FRC | Replaced new light bulb | [6 empty] | Two light fused-Ming Cai-low
FID5641 | Plumbing & Sanitary | Water Heater | Other: tap broken | Localised to room | RMG > RH > 8 > Stn D Pantry |  | 2022-01-07 12:09:27 | 2022-01-07 12:13:23 | 2022-01-07 12:17:30 | 2022-01-07 12:18:09 | 2022-01-07 12:18:32 | 2022-01-07 18:28:05 | Muthu Sathasivam | replace tap | [6 empty] | Hot water tap spoilt-satha-low
FID5619 | Office and Furniture | Wall Clock | Cannot open / close | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-07 07:46:51 | 2022-01-07 07:59:32 | 2022-01-07 08:00:14 | 2022-01-07 08:01:17 | 2022-01-07 08:01:54 | 2022-01-07 08:04:41 | Rajendran Manikandan | adjusted time normal back | [6 empty] | display clock time slow -mani-low
FID5618 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 969 - 970 |  | 2022-01-07 07:40:33 | 2022-01-07 07:41:03 | 2022-01-07 07:41:51 | 2022-01-07 07:42:22 | 2022-01-07 07:42:53 | 2022-01-07 07:43:59 | Rajendran Manikandan | Reset normal back | [6 empty] | call bell keep ringing-mani-low
FID5617 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > A&E Main Counter |  | 2022-01-07 07:32:08 | 2022-01-07 07:32:35 | 2022-01-07 07:33:26 | 2022-01-07 07:33:56 | 2022-01-07 07:34:21 | 2022-01-07 07:36:33 | Rajendran Manikandan | Replaced new bulb | [6 empty] | light fused-mani-low
FID5610 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1052 |  | 2022-01-06 20:05:01 | 2022-01-06 20:06:49 | 2022-01-06 20:07:13 | 2022-01-06 20:07:36 | 2022-01-06 20:08:11 | 2022-01-06 20:12:45 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 24to22 damper position 20to7o auto ingress make it cool | [6 empty] | Aircon too warm, make it cool-v.bala-low
FID5608 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1037 |  | 2022-01-06 19:38:59 | 2022-01-06 19:40:20 | 2022-01-06 19:40:58 | 2022-01-06 19:41:24 | 2022-01-06 19:41:49 | 2022-01-06 19:43:36 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 24to25 make it warm | [6 empty] | Aircon make it warm-v.bala-low
FID5606 | Office and Furniture | TV | Cannot open / close | Affecting Public | RMG > RSC > 13 > Urology Ctr Waiting |  | 2022-01-06 19:14:31 | 2022-01-06 19:20:54 | 2022-01-06 19:21:21 | 2022-01-06 19:21:50 | 2022-01-06 19:23:09 | 2022-01-06 19:23:46 | Vadivelu Balasubramanian | replaced battery | [6 empty] | TV not working-v.bala-low
FID5598 | Building | Ceiling | Leaking | More than 1 room | RMG > RH > 7 > Operating Theatre 4 |  | 2022-01-06 16:30:20 | 2022-01-07 11:38:55 | 2022-01-07 11:39:30 | 2022-01-07 11:40:00 | 2022-01-07 11:40:50 | 2022-01-07 11:54:11 | Hossain | onsite check & foud OR 4 Shadowless operating lamp inside got abit condensation. Wipe up the water & adjusted the temperature setpoint & monitor back to normal. |  |  |  |  | 1 |  | Water leaking from ceiling-hossain-low
FID5596 | Medical Equipment | CSSD Sterilisers | Alarm | More than 1 room | RMG > RH > 7 > CSSD |  | 2022-01-06 16:24:29 | 2022-01-06 16:24:54 | 2022-01-06 16:25:15 | 2022-01-06 16:25:40 | 2022-01-06 16:25:48 | 2022-01-06 16:27:29 | Muthu Shanmugavelu | checked onsite and released the push button , sterliser back to normal.. | [6 empty] | Sterliser 1 got emergency shutdown alarm-Shanmu-medium
FID5595 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1030 |  | 2022-01-06 16:22:33 | 2022-01-06 16:24:19 | 2022-01-06 16:34:10 | 2022-01-06 16:35:27 | 2022-01-06 16:37:27 | 2022-01-06 16:43:19 | Arasan Balasubramanian | adjust the aircon temprature aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-a.bala-low
FID5593 | Plumbing & Sanitary | WC / Squatting Pedestal | Damaged / Loose / Cracked | Localised to room | RMG > RH > 10 > Ward 1010 |  | 2022-01-06 15:29:55 | 2022-01-19 12:08:32 | 2022-01-19 12:08:49 | 2022-01-19 12:09:09 | 2022-01-19 12:09:29 | 2022-01-19 12:10:11 | Chang Fook Keong Alan | I have tightened the seat cover | [6 empty] | Toilet seat cover loose-Allan-low
FID5592 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Nursing Stn B |  | 2022-01-06 15:28:45 | 2022-01-06 16:07:27 | 2022-01-06 16:09:37 | 2022-01-06 16:13:23 | 2022-01-06 16:14:39 | 2022-01-06 16:17:17 | Arasan Balasubramanian | adjusted the temprature aircon make it warm |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID5590 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1062 |  | 2022-01-06 15:11:05 | 2022-01-06 15:19:30 | 2022-01-26 11:11:15 | 2022-01-26 11:16:41 | 2022-01-26 11:17:11 | 2022-01-26 11:17:41 | FRC | Adjusted the aircon temperature in bms system make it cool |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID5589 | Office and Furniture | TV | Cannot open / close | Affecting Public | RMG > RSC > 13 > Urology Ctr Waiting |  | 2022-01-06 15:01:37 | 2022-01-06 15:34:12 | 2022-01-06 19:16:00 | 2022-01-06 19:16:29 | 2022-01-06 19:17:01 | 2022-01-06 19:18:30 | Vadivelu Balasubramanian | program back to normal |  |  |  |  | 1 |  | TV not working-v.bala-low
FID5588 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 11 > Room 1112 (Medisave off) |  | 2022-01-06 14:57:18 | 2022-01-06 15:06:02 | 2022-01-06 15:09:45 | 2022-01-06 15:10:15 | 2022-01-06 15:14:43 | 2022-01-06 15:19:31 | Sivalingam Ilayaraja | adjested the damper then normal back |  |  |  |  | 1 |  | Aircon make it cold-ilayaraja-low
FID5586 | Medical Equipment | Hygrometer | Other: change battery | Affecting Public | RMG > RH > 7 > Angio Suite |  | 2022-01-06 14:53:50 | 2022-01-06 19:20:23 | 2022-01-06 19:25:39 | 2022-01-06 19:26:16 | 2022-01-06 19:26:41 | 2022-01-06 19:27:33 | Vadivelu Balasubramanian | replaced battery |  |  |  |  | 1 |  | Hygrometer need to change battery-v.bala-low
FID5583 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Counter A |  | 2022-01-06 14:40:20 | 2022-01-06 15:14:27 | 2022-01-06 15:14:57 | 2022-01-06 15:23:26 | 2022-01-06 15:33:45 | 2022-01-06 15:57:20 | Arasan Balasubramanian | adjusted the temprature make it cold |  |  |  |  | 1 |  | Aircon make it cool-a.bala-low
FID5581 | Medical Equipment | Fridges & Freezers | Other: Fridge temprature out of range | Affecting Public | RMG > RH > 8 > Nursing Stn D |  | 2022-01-06 14:37:12 | 2022-01-06 15:25:36 | 2022-01-06 16:19:57 | 2022-01-26 11:08:37 | 2022-01-26 11:08:57 | 2022-01-26 11:09:36 | FRC | Checked and rectified |  |  |  |  | 1 |  | Medical fridge temperature out of range-ilayaraja-medium
FID5574 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 13 > Ward 1345-1350 |  | 2022-01-06 12:48:06 | 2022-01-06 16:45:43 | 2022-01-06 16:46:16 | 2022-01-06 16:49:06 | 2022-01-06 17:46:18 | 2022-01-06 17:47:24 | Arasan Balasubramanian | replaced new light fitting | [6 empty] | Bed head light not working-a.bala-low
FID5573 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 7 > OT |  | 2022-01-06 12:45:32 | 2022-01-06 12:52:35 | 2022-01-06 12:53:53 | 2022-01-06 13:36:24 | 2022-01-26 11:07:16 | 2022-01-26 11:07:55 | FRC | Replaced new CO2 cylinder | [6 empty] | Need to replace 1 co2 big cylinder-ilayaraja-medium
FID5571 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 13 > Ward 1358-1363 Nurse Station |  | 2022-01-06 12:11:02 | 2022-01-06 17:48:17 | 2022-01-06 17:48:43 | 2022-01-06 17:49:14 | 2022-01-06 17:49:48 | 2022-01-06 17:52:49 | Arasan Balasubramanian | reset back to normal | [6 empty] | Call bell wire loose-a.bala-low
FID5569 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 1 > Level 1 |  | 2022-01-06 12:00:46 | 2022-01-06 17:54:27 | 2022-01-06 17:55:34 | 2022-01-06 17:56:35 | 2022-01-06 17:59:25 | 2022-01-06 18:00:34 | Arasan Balasubramanian | replaced new light bulb | [6 empty] | Light fused-a.bala-low
FID5568 | Office and Furniture | Safe Box | Cannot open / close | Localised to room | RMG > RH > 8 > Ward 851 |  | 2022-01-06 11:54:17 | 2022-01-26 10:52:33 | 2022-01-26 10:52:55 | 2022-01-26 10:54:57 | 2022-01-26 10:55:38 | 2022-01-26 10:57:28 | FRC | Used master key to open the safe box | [6 empty] | Safe box need to open-a.bala-low
FID5567 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 701 |  | 2022-01-06 11:46:13 | 2022-01-06 13:00:04 | 2022-01-06 13:00:41 | 2022-01-06 13:01:30 | 2022-01-06 13:02:06 | 2022-01-06 13:03:04 | Muthu Sathasivam | adjusted the temperature | [6 empty] | Aircon too cold, make it warm-satha-low
FID5551 | Office and Furniture | TV | Cannot open / close | Localised to room | RMG > RH > 9 > Ward 969 - 970 |  | 2022-01-06 08:59:11 | 2022-01-06 10:44:12 | 2022-01-06 10:44:56 | 2022-01-06 10:45:36 | 2022-01-06 10:46:24 | 2022-01-06 10:47:53 | Sivalingam Ilayaraja | reset the power then on back | [6 empty] | TV not working-ilayaraja-low
FID5549 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-06 08:56:19 | 2022-01-06 13:24:08 | 2022-01-26 10:42:54 | 2022-01-26 10:43:17 | 2022-01-26 10:45:29 | 2022-01-26 10:48:30 | FRC | Adjusted the room vav temperature setpoint and damper position in bms system make it cool | [6 empty] | aircon make it cool -aru-low
FID5548 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 9 > Ward 911 |  | 2022-01-06 08:50:13 | 2022-01-07 07:26:06 | 2022-01-07 07:27:03 | 2022-01-07 07:27:31 | 2022-01-07 07:27:56 | 2022-01-07 07:29:39 | Rajendran Manikandan | Replaced new bulb | [6 empty] | light fused -mani-low
FID5541 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > Angio Suite |  | 2022-01-05 20:11:53 | 2022-01-05 20:17:41 | 2022-01-05 20:18:34 | 2022-01-05 20:19:22 | 2022-01-05 20:37:37 | 2022-01-05 20:39:34 | Arasan Balasubramanian | replaced new light bulb |  |  |  |  | 1 |  | Exit light flickering-a.bala-low
FID5540 | Electrical | Light Driver | Flickering / Blown | Affecting Public | RMG > RSC > 12 > Rehab Ctr T17 |  | 2022-01-05 19:57:20 | 2022-01-05 20:04:16 | 2022-01-05 20:04:54 | 2022-01-05 20:05:20 | 2022-01-05 20:05:48 | 2022-01-05 20:07:30 | Arasan Balasubramanian | replaced light driver |  |  |  |  | 1 |  | Light fused-a.bala-low
FID5538 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 11 > Room 1108 (FAC) |  | 2022-01-05 19:17:02 | 2022-01-05 19:18:13 | 2022-01-05 19:18:37 | 2022-01-05 19:19:01 | 2022-01-05 19:19:27 | 2022-01-05 19:23:12 | Vadivelu Balasubramanian | adjusted temperature in bms 11-2 ahu speed control 50to40 reduce aircon make it warm | [6 empty] | Aircon too cold, make it warm-v.bala-low
FID5535 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-05 17:46:41 | 2022-01-05 17:49:49 | 2022-01-05 17:50:51 | 2022-01-05 17:51:55 | 2022-01-05 18:02:18 | 2022-01-05 18:04:42 | Arasan Balasubramanian | adjust the temprature make it cold |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID5534 | Medical Equipment | Medical Gas | Change Cylinders | Affecting Public | RMG > RH > 7 > OT |  | 2022-01-05 17:34:19 | 2022-01-05 17:35:27 | 2022-01-05 17:36:00 | 2022-01-05 17:36:12 | 2022-01-05 17:36:28 | 2022-01-05 17:37:23 | Muthu Shanmugavelu | delivered 2 nos N2o to OT |  |  |  |  | 1 |  | Need to replace 2 nitrous oxide cylinder-shanmu-medium
FID5524 | Plumbing & Sanitary | Tap | Damaged / Loose / Cracked | Affecting Public | RMG > RH > 2 > Healthcheck Handicap Toilet |  | 2022-01-05 15:57:13 | 2022-01-06 09:45:39 | 2022-01-06 09:45:59 | 2022-01-06 09:46:20 | 2022-01-06 09:46:41 | 2022-01-06 09:47:16 | Chang Fook Keong Alan | Have tied back back |  |  |  |  | 1 |  | Pipe faulty-Allan-low
FID5522 | Mechanical | Pneumatic Tube | Missing | More than 1 room | RMG > RH > 2 > RM@RH Counter |  | 2022-01-05 15:43:12 | 2022-01-05 16:09:28 | 2022-01-05 16:09:55 | 2022-01-05 16:45:04 | 2022-01-05 16:45:49 | 2022-01-05 16:50:09 | Muthu Shanmugavelu | tubes found an return back to station |  |  |  |  | 1 |  | Pneumatic tube alarm-Allan-low
FID5520 | Medical Equipment | Patient Bed | Other: Cannot operate the bed | More than 1 room | RMG > RH > 13 > Ward 1319-1327 Nurse Station |  | 2022-01-05 15:22:40 | 2022-01-26 10:26:38 | 2022-01-26 10:27:00 | 2022-01-26 10:27:20 | 2022-01-26 10:27:43 | 2022-01-26 10:28:11 | FRC | Repaired the bed |  |  |  |  | 1 |  | Patient bed not working-ming cai-low
FID5514 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 11 > Room 1112 (Medisave off) |  | 2022-01-05 14:31:31 | 2022-01-26 10:19:08 | 2022-01-26 10:24:07 | 2022-01-26 10:24:27 | 2022-01-26 10:24:57 | 2022-01-26 10:25:43 | FRC | Manually open the damper onsite to make the room cool |  |  |  |  | 1 |  | Aircon make cold-v.bala-low
FID5513 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU |  | 2022-01-05 14:27:36 | 2022-01-05 14:45:51 | 2022-01-05 14:46:43 | 2022-01-05 15:24:57 | 2022-01-05 15:58:41 | 2022-01-05 16:00:35 | Arasan Balasubramanian | adjusted temprature make it cold |  |  |  |  | 1 |  | Aircon make it cold-a.bala-low
FID5512 | Medical Equipment | Medical Gas | Alarm | Whole Building | RMG > RH > 3 > Medical Compressed Air Rm |  | 2022-01-05 14:23:24 | 2022-01-05 14:24:05 | 2022-01-05 14:24:26 | 2022-01-05 14:24:48 | 2022-01-05 14:25:09 | 2022-01-26 10:18:22 | FRC | Checked and rectified | [6 empty] | Medical air panel alarming-Shanmu-medium
FID5509 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 11 > Room 1108 (FAC) |  | 2022-01-05 12:42:10 | 2022-01-26 10:15:19 | 2022-01-26 10:15:38 | 2022-01-26 10:15:58 | 2022-01-26 10:16:17 | 2022-01-26 10:16:53 | FRC | Manually close the damper onsite to make warm | [6 empty] | Aircon too cold, make it warm-v.bala-low
FID5508 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 2 > RM@RH Consult Rm 3 |  | 2022-01-05 12:28:42 | 2022-01-05 12:29:21 | 2022-01-05 12:29:52 | 2022-01-05 12:30:16 | 2022-01-05 12:30:44 | 2022-01-05 12:34:48 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 24to22 damper position auto never change manually put 70 | [6 empty] | Aircon too warm-v.bala-low
FID5499 | Medical Equipment | AGSS | Alarm | More than 1 room | RMG > RH > 7M > Level 7M |  | 2022-01-05 10:58:28 | 2022-01-05 10:58:52 | 2022-01-05 10:59:17 | 2022-01-05 10:59:40 | 2022-01-05 11:01:43 | 2022-01-05 12:32:02 | Muthu Shanmugavelu | Pm service completed by contractor | [6 empty] | AGSS yearly PM service by contractor-Shanmu-low
FID5487 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 2 > RCM Consult Rm 3 |  | 2022-01-05 08:47:16 | 2022-01-26 10:12:31 | 2022-01-26 10:12:52 | 2022-01-26 10:13:13 | 2022-01-26 10:13:37 | 2022-01-26 10:14:26 | FRC | Adjusted the room vav temperature setpoint and damper position make it cool in bms system | [6 empty] | Aircon very warm, need to make cool-ilayaraja-low
FID5484 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RSC > 12 > Rehab Ctr T17 |  | 2022-01-05 08:42:22 | 2022-01-19 12:11:44 | 2022-01-19 12:12:04 | 2022-01-19 12:12:23 | 2022-01-19 12:12:42 | 2022-01-19 12:13:17 | Chang Fook Keong Alan | I have change the new bulb | [6 empty] | Need to replace the ceiling light fused-allan-low
FID5478 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1045 |  | 2022-01-05 02:00:06 | 2022-01-05 02:02:04 | 2022-01-05 02:02:32 | 2022-01-05 02:02:55 | 2022-01-05 02:03:15 | 2022-01-05 02:03:51 | Muthu Sathasivam | adjusted the temperature in bms | [6 empty] | Need to switch off the aircon-satha-low
FID5477 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU |  | 2022-01-05 01:58:17 | 2022-01-05 02:01:32 | 2022-01-05 02:04:18 | 2022-01-05 02:04:46 | 2022-01-05 02:05:05 | 2022-01-05 02:05:46 | Muthu Sathasivam | adjusted the setpoint from 16 to 18 degree | [6 empty] | Aircon make it warm-satha-low
FID5467 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > ICU Rm 703 |  | 2022-01-04 16:43:51 | 2022-01-26 10:08:21 | 2022-01-26 10:09:55 | 2022-01-26 10:10:16 | 2022-01-26 10:10:36 | 2022-01-26 10:11:23 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon too cold, make it warm-su-low
FID5465 | Electrical | Call System | Unserviceable | Localised to room | RMG > RH > 9 > Ward 980 - 986 |  | 2022-01-04 16:17:05 | 2022-01-15 11:26:30 | 2022-01-15 11:26:54 | 2022-01-15 11:27:20 | 2022-01-15 11:27:44 | 2022-01-15 11:28:07 | Li Fei | completed | [6 empty] | Call bell keep ringing-Senthil-low
FID5464 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 12 > REMC RM 3 |  | 2022-01-04 16:14:56 | 2022-01-15 14:19:42 | 2022-01-15 14:21:20 | 2022-01-15 14:21:45 | 2022-01-15 14:22:06 | 2022-01-15 14:22:36 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Ceiling light need to change-mani-low
FID5463 | Building | Door Closer | Noisy | Localised to room | RMG > RH > 8 > Ward 818 |  | 2022-01-04 16:13:06 | 2022-01-05 09:12:42 | 2022-01-05 09:25:26 | 2022-01-05 09:26:11 | 2022-01-05 09:29:21 | 2022-01-05 09:31:14 | Hossain | onsite adjusted the door closer & applied WD 40 back to normal. | [6 empty] | Door noisy-Hossain-low
FID5456 | Office and Furniture | Cabinet | Other: Need to shift the pedestal cabinet | Affecting Public | RMG > RSC > 2 > Corridor |  | 2022-01-04 12:03:18 | 2022-01-04 12:54:03 | 2022-01-04 12:54:25 | 2022-01-04 12:54:51 | 2022-01-04 12:55:19 | 2022-01-04 12:57:01 | Chang Fook Keong Alan | Have send to users at RSC level two | [6 empty] | Need to shift the pedestal cabinet from level 17 to level 2 -Allan-low
FID5455 | Building | Door Knob / Handle | Misaligned / dangling | Affecting Public | RMG > RH > 12 > RHS Female Toilet |  | 2022-01-04 11:55:55 | 2022-01-04 13:38:15 | 2022-01-04 13:38:48 | 2022-01-04 13:39:25 | 2022-01-04 13:40:43 | 2022-01-04 13:43:32 | Hossain | Rectified the door handle back to normal. | [6 empty] | Door handle faulty-Hossain-low
FID5453 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > Day Surgery |  | 2022-01-04 11:03:05 | 2022-01-25 17:54:38 | 2022-01-25 17:54:58 | 2022-01-25 17:55:34 | 2022-01-25 17:55:56 | 2022-01-25 17:56:49 | FRC | Replaced new light | [6 empty] | Light flickering-Senthil-low
FID5452 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 7 > ICU Rm 709 |  | 2022-01-04 11:01:06 | 2022-01-25 17:39:49 | 2022-01-25 17:40:18 | 2022-01-25 17:52:26 | 2022-01-25 17:53:32 | 2022-01-25 17:54:00 | FRC | Reset the call bell system back to normal | [6 empty] | Call bell not working-senthil-low
FID5451 | Plumbing & Sanitary | Floor trap | Choked | Affecting Public | RMG > RSC > 1 > Bin Centre |  | 2022-01-04 10:58:08 | 2022-01-06 14:56:15 | 2022-01-06 14:56:40 | 2022-01-06 14:57:05 | 2022-01-06 14:57:33 | 2022-01-06 14:58:14 | Chang Fook Keong Alan | I have Clear Chok | [6 empty] | Floor trap choke-Allan-low
FID5450 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 8 > NICU |  | 2022-01-04 10:57:00 | 2022-01-04 11:01:14 | 2022-01-04 11:30:35 | 2022-01-04 11:31:13 | 2022-01-04 11:32:02 | 2022-01-04 11:33:21 | Arasan Balasubramanian | replaced new light bulb | [6 empty] | light flickering-a.bala-low
FID5444 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1061 |  | 2022-01-04 10:21:17 | 2022-01-25 17:28:27 | 2022-01-25 17:28:49 | 2022-01-25 17:29:10 | 2022-01-25 17:29:32 | 2022-01-25 17:30:15 | FRC | Adjusted the room vav temperature setpoint and damper position in bms system make it warm | [6 empty] | Aircon make it warm-Aru-low
FID5443 | Building | Door Closer | Unable to open or close properly | Affecting Public | RMG > RH > 11 > Learning Ctr - Corridor |  | 2022-01-04 10:20:18 | 2022-01-04 12:59:05 | 2022-01-04 12:59:26 | 2022-01-04 12:59:47 | 2022-01-04 13:00:09 | 2022-01-04 13:01:16 | Chang Fook Keong Alan | Contactor have fixed back the door | [6 empty] | Door faulty-Allan-low
FID5442 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1029 |  | 2022-01-04 10:19:10 | 2022-01-25 17:32:04 | 2022-01-25 17:33:11 | 2022-01-25 17:33:38 | 2022-01-25 17:33:59 | 2022-01-25 17:34:47 | FRC | Adjusted the room vav temperature setpoint and damper position make it warm in bms system | [6 empty] | Aircon make it warm-Aru-low
FID5441 | Office and Furniture | TV | Other: TV cannot hear the sound | Affecting Public | RMG > RH > 10 > Ward 1061 |  | 2022-01-04 10:17:53 | 2022-01-25 17:37:22 | 2022-01-25 17:37:47 | 2022-01-25 17:38:10 | 2022-01-25 17:38:29 | 2022-01-25 17:39:01 | FRC | Adjusted the TV settings | [6 empty] | TV cannot hear the sound-Senthil-low
FID5440 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1061 |  | 2022-01-04 10:16:52 | 2022-01-25 17:26:02 | 2022-01-25 17:26:23 | 2022-01-25 17:26:43 | 2022-01-25 17:27:04 | 2022-01-25 17:27:41 | FRC | Adjusted the room vav temperature setpoint and damper position in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID5439 | Building | Window | Other: Need to close | Affecting Public | RMG > RH > 8 > Ward 833 (Victoria Suite) |  | 2022-01-04 10:15:25 | 2022-01-05 08:59:03 | 2022-01-05 08:59:21 | 2022-01-05 08:59:41 | 2022-01-05 08:59:59 | 2022-01-05 09:00:23 | liumingcai | close | [6 empty] | Need to close the window-Ming cai-low
FID5438 | Building | Water Dispenser | Leaking | Affecting Public | RMG > RH > 9 > Stn D Pantry |  | 2022-01-04 10:14:30 | 2022-01-04 13:02:32 | 2022-01-04 13:02:53 | 2022-01-04 13:03:26 | 2022-01-04 13:03:59 | 2022-01-04 13:05:10 | Chang Fook Keong Alan | We fix the leaking | [6 empty] | Water dispenser leaking-Allan, Aru-low
FID5436 | Building | Filter | Leaking | Localised to room | RMG > RH > 7 > CSSD |  | 2022-01-04 09:42:17 | 2022-01-25 17:22:50 | 2022-01-25 17:23:10 | 2022-01-25 17:23:34 | 2022-01-25 17:23:56 | 2022-01-25 17:25:05 | FRC | Tighten the filter properly | [6 empty] | Filter leaking-v.bala-low
FID5435 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 1 > Nuclear Medicine Centre |  | 2022-01-04 09:40:21 | 2022-01-04 09:59:08 | 2022-01-04 09:59:36 | 2022-01-04 10:00:04 | 2022-01-04 10:00:43 | 2022-01-04 10:26:03 | FRC | Adjusted AHU 1-5 temperature setpoint from 23c to 21c in bms system make it cool | [6 empty] | Aircon make it cool-Su-low
FID5434 | Building | Hand Rail | Misaligned / dangling | Affecting Public | RMG > RH > 8 > Stn D Corridor |  | 2022-01-04 09:21:17 | 2022-01-05 17:42:17 | 2022-01-05 17:42:51 | 2022-01-05 17:43:26 | 2022-01-05 17:44:00 | 2022-01-05 17:47:53 | Hossain | onsite check & fixed back properly the wall guard. | [6 empty] | Handrail dropping-Hossain-low
FID5432 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-04 09:20:01 | 2022-01-04 10:01:27 | 2022-01-04 10:01:50 | 2022-01-04 10:02:12 | 2022-01-04 10:02:49 | 2022-01-04 10:27:01 | FRC | Adjusted vav 1-1-13 temperature setpoint from 24c to 21c in bms system make it cool. Damper position automatically increase from 20% to 90% | [6 empty] | Aircon make it cool-su-low
FID5428 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 7 > ICU Counter A |  | 2022-01-04 08:43:29 | 2022-01-04 09:50:14 | 2022-01-04 09:50:41 | 2022-01-04 09:54:25 | 2022-01-04 09:55:29 | 2022-01-04 10:05:21 | Arasan Balasubramanian | replaced new light bulb | [6 empty] | light flickering-a.bala-low
FID5426 | Medical Equipment | CSSD Sterilisers | Alarm | More than 1 room | RMG > RH > 7 > CSSD Sterilizer Pump Rm |  | 2022-01-04 07:58:43 | 2022-01-25 17:12:33 | 2022-01-25 17:13:12 | 2022-01-25 17:17:05 | 2022-01-25 17:17:52 | 2022-01-25 17:18:21 | FRC | Informed to Getinge contractor to check. Rectified | [6 empty] | Sterilizer showing steam generator issue, need to check-ming cai-low
FID5425 | Building | Door Knob / Handle | Misaligned / dangling | Localised to room | RMG > RH > 12 > Staircase 4 |  | 2022-01-04 07:25:20 | 2022-01-04 07:43:33 | 2022-01-04 07:44:52 | 2022-01-04 07:59:42 | 2022-01-04 08:01:26 | 2022-01-04 08:02:42 | Sivalingam Ilayaraja | screw thigten back to normol | [6 empty] | Door handle spoilt-ilayaraja-low
FID5424 | Mechanical | Air Diffuser (supply/return) | Airflow too strong / weak | Localised to room | RMG > RH > 8 > Ward 816 |  | 2022-01-04 07:22:41 | 2022-01-04 07:27:07 | 2022-01-04 07:28:04 | 2022-01-04 07:28:52 | 2022-01-04 07:29:24 | 2022-01-04 07:30:03 | Muthu Sathasivam | close air diffuser | [6 empty] | Aircon make warm-satha-low
FID5409 | Medical Equipment | Medical Gas | Change Cylinders | Localised to room | RMG > RH > 2 > Dental Clinic |  | 2022-01-03 16:08:36 | 2022-01-03 16:09:07 | 2022-01-03 16:10:13 | 2022-01-03 16:12:21 | 2022-01-03 16:15:46 | 2022-01-03 16:18:37 | Muthu Shanmugavelu | delivered 2 O2 cop cylinders to dental | [6 empty] | Need to supply 2 oxygen cop cylinders-Shanmu-medium
FID5405 | Medical Equipment | CSSD Sterilisers | Alarm | Localised to room | RMG > RH > 7 > CSSD |  | 2022-01-03 15:58:56 | 2022-01-03 15:59:20 | 2022-01-03 15:59:39 | 2022-01-03 16:00:00 | 2022-01-03 16:00:27 | 2022-01-03 16:01:29 | Muthu Shanmugavelu | Adjusted the brightness for sterliser 2..informed the user. | [6 empty] | Steriliser 2 display is darker than usual display-shanmu-low
FID5403 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 7 > ICU Rm 705 |  | 2022-01-03 15:43:32 | 2022-01-25 16:59:32 | 2022-01-25 16:59:53 | 2022-01-25 17:00:34 | 2022-01-25 17:01:01 | 2022-01-25 17:06:04 | FRC | Reset the call bell system back to normal | [6 empty] | Call bell not working-senthil-low
FID5402 | Medical Equipment | Medical Gas | Alarm | Affecting Public | RMG > RH > 9 > Nursing Stn A |  | 2022-01-03 15:36:20 | 2022-01-03 15:49:05 | 2022-01-03 15:49:25 | 2022-01-03 15:49:45 | 2022-01-03 15:50:05 | 2022-01-03 15:51:53 | Muthu Shanmugavelu | checked onsite got rccb tripped at sub dB.. reset back to normal | [6 empty] | Medical gas panel alarming-Shanmu-medium
FID5401 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > 25 Tannery Lane > 3 > TL-3-25 Office |  | 2022-01-03 15:34:23 | 2022-01-25 16:56:18 | 2022-01-25 16:56:47 | 2022-01-25 16:57:37 | 2022-01-25 16:58:09 | 2022-01-25 16:58:38 | FRC | Replaced new light | [6 empty] | Light flickering-Ela-low
FID5394 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 7 > OT Clean Corridor |  | 2022-01-03 14:48:27 | 2022-01-25 16:53:16 | 2022-01-25 16:53:41 | 2022-01-25 16:54:07 | 2022-01-25 16:54:29 | 2022-01-25 16:55:37 | FRC | Adjusted the temperature setpoint for the AHU in bms system | [6 empty] | Humidity showing 60.5% and temperature 18.5c, out of range-satha-low
FID5393 | Mechanical | AHU / FCU / CU | Other: Humidity out of range | Affecting Public | RMG > RH > 7 > CSSD |  | 2022-01-03 14:45:49 | 2022-01-03 22:50:32 | 2022-01-03 22:50:59 | 2022-01-03 22:51:37 | 2022-01-03 22:52:36 | 2022-01-03 22:54:01 | Muthu Sathasivam | adjusted the setpoint temperature | [6 empty] | Humidity showing 60.3%, out of range-satha-low
FID5392 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 2 > RM@RH Consult Rm 3 |  | 2022-01-03 14:44:29 | 2022-01-03 14:49:26 | 2022-01-03 14:49:48 | 2022-01-03 14:51:18 | 2022-01-03 14:51:38 | 2022-01-04 10:29:14 | FRC | Adjusted VAV 1-1-14 temperature setpoint from 20c to 24c in bms system make it warm. Damper position automatically reduce from 90% to 20% | [6 empty] | Aircon too cold, make it warm-Su-low
FID5391 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1029 |  | 2022-01-03 14:40:18 | 2022-01-03 14:52:16 | 2022-01-03 14:56:34 | 2022-01-03 14:56:55 | 2022-01-03 14:57:16 | 2022-01-25 16:52:09 | FRC | Adjusted the room vav damper position in bms system make it warm | [6 empty] | Aircon too cold, make it warm-Su-low
FID5387 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 9 > Business Centre Office 1 |  | 2022-01-03 14:16:38 | 2022-01-03 15:44:58 | 2022-01-03 15:45:18 | 2022-01-03 15:45:39 | 2022-01-03 15:46:15 | 2022-01-03 15:47:03 | Chang Fook Keong Alan | The light bulb change already | [6 empty] | Light fused-allan-low
FID5383 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 7 > OT Soiled Utility Rm (beside OR4) |  | 2022-01-03 12:12:18 | 2022-01-03 13:21:03 | 2022-01-03 13:21:32 | 2022-01-03 13:21:55 | 2022-01-03 13:22:20 | 2022-01-03 13:23:08 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light fused-mani-low
FID5382 | Electrical | Light Bulb | Tripped / Short-Circuit / Overloaded | Affecting Public | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-03 12:09:47 | 2022-01-03 13:23:48 | 2022-01-03 13:24:14 | 2022-01-03 13:24:47 | 2022-01-03 13:25:10 | 2022-01-03 13:26:12 | Rajendran Manikandan | Mcb trip and Reset normalback | [6 empty] | No light, power trip-mani-high
FID5374 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 1 > Nuclear Medicine Centre |  | 2022-01-03 11:28:16 | 2022-01-25 16:47:59 | 2022-01-25 16:48:34 | 2022-01-25 16:48:56 | 2022-01-25 16:49:49 | 2022-01-25 16:50:32 | FRC | Adjusted the aircon temperature in bms system make it warm | [6 empty] | Aircon too cold, make it warm-Su-low
FID5373 | Medical Equipment | Fridges & Freezers | Other: Fridge not cold | Affecting Public | RMG > RH > 11 > Office Pantry |  | 2022-01-03 11:20:54 | 2022-01-25 16:45:24 | 2022-01-25 16:45:48 | 2022-01-25 16:46:09 | 2022-01-25 16:46:29 | 2022-01-25 16:47:13 | FRC | Fridge spoilt, unable to repair. Need to replace new. Pending | [6 empty] | Fridge not cold-Aru-low
FID5372 | Electrical | PA System | Other: Music too loud | Affecting Public | RMG > RH > 2 > Skin & Aesthetics Clinic |  | 2022-01-03 11:15:54 | 2022-01-25 16:42:04 | 2022-01-25 16:42:26 | 2022-01-25 16:43:23 | 2022-01-25 16:43:44 | 2022-01-25 16:44:24 | FRC | Adjusted the PA system console | [6 empty] | Music volume too loud-senthil-low
FID5371 | Mechanical | AHU / FCU / CU | Other: Smell | Affecting Public | RMG > RH > 7 > Day Surgery Corridor |  | 2022-01-03 11:14:50 | 2022-01-25 16:36:44 | 2022-01-25 16:37:03 | 2022-01-25 16:37:25 | 2022-01-25 16:37:47 | 2022-01-25 16:41:23 | FRC | Upon reaching onsite, the smell is slowly going off, unable to find the source. Informed to user to monitor and highlight again if smell occur. | [6 empty] | Burning smell from day surgery through or1 till corridor outside reprocessing rm - senthil-medium
FID5370 | Electrical | Call System | Unserviceable | Affecting Public | RMG > RH > 10 > Ward 1043 |  | 2022-01-03 11:09:30 | 2022-01-15 12:19:28 | 2022-01-15 19:57:19 | 2022-01-15 19:57:41 | 2022-01-15 19:58:02 | 2022-01-15 19:58:38 | Rajendran Manikandan | Reset normal back | [6 empty] | Call bell cannot turn off-Mani-low
FID5368 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 8 > Ward 809 |  | 2022-01-03 10:48:24 | 2022-01-25 16:30:33 | 2022-01-25 16:30:54 | 2022-01-25 16:31:29 | 2022-01-25 16:33:41 | 2022-01-25 16:34:10 | FRC | Cleared the basin choke | [6 empty] | Basin choke-V.Bala-low
FID5367 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1030 |  | 2022-01-03 10:47:19 | 2022-01-25 15:55:22 | 2022-01-25 15:57:06 | 2022-01-25 16:05:13 | 2022-01-25 16:05:38 | 2022-01-25 16:17:33 | FRC | Adjusted the aircon temperature in bms system make it cool | [6 empty] | Aircon make it cool-V.Bala-low
FID5366 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 1 > Nuclear Med PET/CT |  | 2022-01-03 10:43:25 | 2022-01-03 11:36:41 | 2022-01-03 11:37:19 | 2022-01-03 11:38:00 | 2022-01-03 11:38:39 | 2022-01-03 11:40:19 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light fused 2 nos-mani-low
FID5365 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > 25 Tannery Lane > 7 > TL-7-27 Office |  | 2022-01-03 10:42:32 | 2022-01-15 11:49:19 | 2022-01-15 11:51:17 | 2022-01-15 11:51:45 | 2022-01-15 11:56:42 | 2022-01-15 11:57:21 | Li Fei | done by ella | [6 empty] | Light flickering-Ela-low
FID5364 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 1 > Nuclear Medicine Centre |  | 2022-01-03 10:41:32 | 2022-01-25 15:52:42 | 2022-01-25 15:53:04 | 2022-01-25 15:53:25 | 2022-01-25 15:53:52 | 2022-01-25 15:54:38 | FRC | Adjusted AHU 1-5 temperature setpoint in bms system make it cool | [6 empty] | Aircon very warm-aru-low
FID5363 | Electrical | PA System | Unserviceable | Affecting Public | RMG > RH > 7 > Call Centre |  | 2022-01-03 10:40:44 | 2022-01-15 11:45:02 | 2022-01-15 11:45:38 | 2022-01-15 11:46:31 | 2022-01-15 11:47:59 | 2022-01-15 11:48:23 | Li Fei | done | [6 empty] | PA console for code blue got red light indicator lighted up-Li Fei-low
FID5362 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 8 > Ward 805 |  | 2022-01-03 10:38:23 | 2022-01-25 15:49:38 | 2022-01-25 15:50:08 | 2022-01-25 15:50:37 | 2022-01-25 15:50:59 | 2022-01-25 15:51:39 | FRC | Checked and found water leaking from the bidet spray hose. Replaced new bidet spray hose, back to normal | [6 empty] | Water leaking from the pipe-ming cai-low
FID5359 | Plumbing & Sanitary | Basin / sink | Choked | Affecting Public | RMG > RH > 7 > OT Female Changing Rm |  | 2022-01-03 10:33:46 | 2022-01-25 15:46:15 | 2022-01-25 15:46:35 | 2022-01-25 15:46:56 | 2022-01-25 15:47:19 | 2022-01-25 15:47:50 | FRC | Basin clogged. Cleared the choke, back to normal | [6 empty] | Basin water flow very slow-Ming Cai-low
FID5358 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 1 > Unit #01-06 |  | 2022-01-03 10:32:30 | 2022-01-25 15:39:17 | 2022-01-25 15:43:31 | 2022-01-25 15:44:24 | 2022-01-25 15:44:45 | 2022-01-25 15:45:26 | FRC | Checked and found the FCU was manual off in bms system. Put back to auto mode, FCU running back to normal. | [6 empty] | Aircon not working-su-low
FID5357 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2022-01-03 10:31:13 | 2022-01-03 11:59:34 | 2022-01-03 11:59:58 | 2022-01-03 12:00:27 | 2022-01-03 12:00:49 | 2022-01-03 12:01:57 | FRC | Adjusted vav 1-1-25 temperature setpoint from 24c to 26c and damper position from 10% manual to 0% manual in bms system make it warm | [6 empty] | Aircon make it warm -Su-low
FID5355 | Electrical | PA System | Other: Music too loud | Affecting Public | RMG > RSC > 16 > Eye Centre |  | 2022-01-03 10:21:56 | 2022-01-15 11:39:52 | 2022-01-15 11:40:39 | 2022-01-15 11:41:02 | 2022-01-15 11:41:41 | 2022-01-15 11:42:22 | Li Fei | done | [6 empty] | Music volume too loud-senthil-low
FID5354 | Electrical | Light Bulb | Flickering / Blown | Affecting Public | RMG > RH > 13 > Passenger Lift Lobby |  | 2022-01-03 10:20:46 | 2022-01-03 10:36:54 | 2022-01-03 10:37:29 | 2022-01-03 10:37:55 | 2022-01-03 10:38:31 | 2022-01-03 10:48:37 | Rajendran Manikandan | Replaced new drivers | [6 empty] | Light flickering-mani-low
FID5346 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 12 > Women Centre Consult Rm 7 |  | 2022-01-03 08:43:37 | 2022-01-06 15:02:17 | 2022-01-06 15:02:41 | 2022-01-06 15:03:05 | 2022-01-06 15:03:36 | 2022-01-06 15:04:26 | Chang Fook Keong Alan | I have change the bulb |  |  |  |  | 1 |  | Light flickering-allan-low
FID5343 | Plumbing & Sanitary | WC / Squatting Pedestal | Water flowing non-stop | Affecting Public | RMG > RH > 9 > Stn A Soiled Utility Rm |  | 2022-01-03 08:18:27 | 2022-01-03 08:58:00 | 2022-01-03 08:58:19 | 2022-01-03 08:58:38 | 2022-01-03 08:58:56 | 2022-01-03 09:27:00 | liumingcai | repaired | [6 empty] | WC water non stop flushing-ming cai-low
FID5339 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 7 > ICU Counter A |  | 2022-01-03 01:53:09 | 2022-01-25 15:36:21 | 2022-01-25 15:36:42 | 2022-01-25 15:37:03 | 2022-01-25 15:37:24 | 2022-01-25 15:38:11 | FRC | Adjusted the aircon temperature in bms system make it warm |  |  |  |  | 1 |  | aircon make it warm-v.bala-low
FID5338 | Plumbing & Sanitary | Basin / sink | Choked | More than 1 room | RMG > RH > 8 > Ward 809 |  | 2022-01-03 00:19:40 | 2022-01-03 01:23:05 | 2022-01-03 01:23:31 | 2022-01-03 01:23:54 | 2022-01-03 01:24:23 | 2022-01-03 01:26:00 | Vadivelu Balasubramanian | basin choke cleared |  |  |  |  | 1 |  | Basin choke-v.bala-low
FID5337 | Mechanical | AHU / FCU / CU | Airflow too strong / weak | More than 1 room | RMG > RH > 10 > Ward 1030 |  | 2022-01-02 23:50:49 | 2022-01-03 01:26:59 | 2022-01-03 01:27:35 | 2022-01-03 01:28:09 | 2022-01-03 01:28:49 | 2022-01-03 01:33:19 | Vadivelu Balasubramanian | adjusted temperature in bms vav control damper position 50to70 make it cool | [6 empty] | Aircon make cool-V.Bala-low
FID5329 | Mechanical | Pneumatic Tube | Other: ALRAM ON PTS SYSTEM | Localised to room | RMG > RH > 2 > RM@RH |  | 2022-01-02 17:39:50 | 2022-01-02 17:40:20 | 2022-01-02 17:40:42 | 2022-01-02 17:41:03 | 2022-01-02 17:41:29 | 2022-01-02 17:42:43 | Muthu Shanmugavelu | checked and found system working normal.. | [6 empty] | Pneumatic tube alarming-shanmu-low
FID5328 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 10 > Bed Lift Lobby |  | 2022-01-02 16:57:01 | 2022-01-02 17:06:31 | 2022-01-02 17:06:57 | 2022-01-02 18:22:11 | 2022-01-02 18:22:54 | 2022-01-02 18:23:52 | Sivalingam Ilayaraja | replaced the new loght | [6 empty] | Spot light fused-ilayaraja-low
FID5327 | Mechanical | BMS / BAS | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1029 |  | 2022-01-02 16:48:07 | 2022-01-02 16:49:10 | 2022-01-02 16:49:57 | 2022-01-02 16:50:24 | 2022-01-02 16:50:56 | 2022-01-02 16:51:40 | Muthu Sathasivam | adjusted the setpoint temperature in bms | [6 empty] | Aircon make it warm-satha-low
FID5326 | Office and Furniture | Wall Clock | Other: digital clock timing need to change | Localised to room | RMG > RH > 13 > Level 13 |  | 2022-01-02 16:46:38 | 2022-01-15 11:37:31 | 2022-01-15 11:37:55 | 2022-01-15 11:38:20 | 2022-01-15 11:38:43 | 2022-01-15 11:39:06 | Li Fei | done | [6 empty] | Need to change timing for digital clock-mani-low
FID5319 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 9 > Ward 956 - 959 (Lab admin) |  | 2022-01-02 11:50:13 | 2022-01-25 15:34:02 | 2022-01-25 15:34:23 | 2022-01-25 15:34:43 | 2022-01-25 15:35:03 | 2022-01-25 15:35:31 | FRC | Cleared the basin choke | [6 empty] | Basin choke-ilayaraja-low
FID5317 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1319-1327 |  | 2022-01-02 11:28:11 | 2022-01-02 11:28:34 | 2022-01-02 11:32:20 | 2022-01-02 11:32:39 | 2022-01-02 11:33:21 | 2022-01-02 11:34:05 | Muthu Sathasivam | adjusted the temperature setpoint | [6 empty] | Aircon make warm-satha-low
FID5314 | Electrical | Call System | Other: Call bell keep ringing | Localised to room | RMG > RH > 10 > Ward 1043 |  | 2022-01-02 10:17:59 | 2022-01-02 11:11:52 | 2022-01-02 11:12:20 | 2022-01-02 11:12:41 | 2022-01-02 11:15:44 | 2022-01-02 11:17:02 | Muthu Shanmugavelu | call Bell faceplate cancel button spoiled..need to be replaced..under followup. | [6 empty] | Call bell keep on ringing-shanmu-low
FID5312 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Affecting Public | RMG > RH > 10 > Ward 1052 |  | 2022-01-02 02:19:30 | 2022-01-02 02:23:22 | 2022-01-02 02:23:57 | 2022-01-02 02:24:24 | 2022-01-02 02:25:03 | 2022-01-02 02:26:35 | Arasan Balasubramanian | adjusted the temprature aircon make it warm |  |  |  |  | 1 |  | Aircon make it warm-a.bala-low
FID5311 | Plumbing & Sanitary | Basin / sink | Choked | Localised to room | RMG > RH > 8 > Delivery Suite 1 |  | 2022-01-02 01:20:15 | 2022-01-02 01:21:20 | 2022-01-02 01:21:45 | 2022-01-02 01:22:08 | 2022-01-02 01:31:14 | 2022-01-02 01:32:39 | Vadivelu Balasubramanian | choke cleared | [6 empty] | Basin choke-v.bala-low
FID5310 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 13 Nurse Counter |  | 2022-01-02 01:11:37 | 2022-01-02 01:24:03 | 2022-01-02 01:24:43 | 2022-01-02 01:27:18 | 2022-01-02 01:27:48 | 2022-01-02 01:30:25 | Vadivelu Balasubramanian | adjusted temperature in bms vav control setpoint 22to24 make it warm | [6 empty] | Aircon too cold-v.bala-low
FID5308 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 10 > Ward 1052 |  | 2022-01-01 19:26:39 | 2022-01-01 19:27:25 | 2022-01-01 19:28:11 | 2022-01-01 19:29:04 | 2022-01-01 19:29:43 | 2022-01-01 19:31:07 | Rajendran Manikandan | adjested the temperature from bms vav then make it warm | [6 empty] | Aircon very cool, make it warm-ilayaraja-low
FID5307 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 9 > Stn D Pantry |  | 2022-01-01 19:23:21 | 2022-01-02 16:30:34 | 2022-01-02 16:31:11 | 2022-01-02 16:31:35 | 2022-01-02 16:36:18 | 2022-01-02 16:37:30 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Ceiling lights not working-mani-low
FID5306 | Mechanical | Ducting | Leaking / Condensation | Affecting Public | RMG > RH > 1 > A&E |  | 2022-01-01 19:19:07 | 2022-01-01 21:12:49 | 2022-01-01 21:13:10 | 2022-01-01 21:13:31 | 2022-01-01 21:14:01 | 2022-01-01 21:15:21 | Chang Fook Keong Alan | Uses say after after 9:30pm do the Water leaking | [6 empty] | Water leaking from ceiling-Allan-low
FID5305 | Electrical | Light Bulb | Flickering / Blown | More than 1 room | RMG > RH > 1 > A&E |  | 2022-01-01 19:07:05 | 2022-01-15 11:31:54 | 2022-01-15 11:32:19 | 2022-01-15 11:32:44 | 2022-01-15 11:34:13 | 2022-01-15 11:34:39 | Li Fei | done | [6 empty] | Ceiling light fused-iskandar-low
FID5304 | Mechanical | AHU / FCU / CU | Too hot / Too cold | More than 1 room | RMG > RH > 9 > Ward 916 |  | 2022-01-01 18:50:34 | 2022-01-01 18:54:49 | 2022-01-01 18:55:26 | 2022-01-01 18:55:59 | 2022-01-01 18:56:33 | 2022-01-01 19:00:08 | Sivalingam Ilayaraja | adjested the temperature from dermoset then make it cool | [6 empty] | Aircon very stuffy, need to make it cool-ilayaraja-low
FID5303 | Plumbing & Sanitary | Bottle Trap | Choked | More than 1 room | RMG > RH > 1 > A&E Handicap Toilet |  | 2022-01-01 18:46:57 | 2022-01-01 21:16:13 | 2022-01-01 21:16:35 | 2022-01-01 21:16:55 | 2022-01-01 21:18:31 | 2022-01-01 21:19:51 | Chang Fook Keong Alan | Toilet choke Have make | [6 empty] | Toilet bowl choke-allan-low
FID5294 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Ward 1052 |  | 2022-01-01 08:14:58 | 2022-01-25 15:30:08 | 2022-01-25 15:31:01 | 2022-01-25 15:31:23 | 2022-01-25 15:32:28 | 2022-01-25 15:33:10 | FRC | Adjusted the temperature setpoint and damper position for the room vav in bms system make it warm | [6 empty] | Aircon make it warm -aru-low
FID5293 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn D |  | 2022-01-01 08:12:44 | 2022-01-15 20:00:29 | 2022-01-15 20:00:57 | 2022-01-15 20:01:18 | 2022-01-15 20:02:06 | 2022-01-15 20:03:40 | Rajendran Manikandan | adjusted the temperature setpoint 20c to 24c bms system make it warm | [6 empty] | Aircon make it warm-mani-low
FID5291 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 10 > Nursing Stn C |  | 2022-01-01 08:00:21 | 2022-01-01 08:00:56 | 2022-01-01 08:02:27 | 2022-01-01 08:02:50 | 2022-01-01 08:03:14 | 2022-01-01 08:09:51 | Rajendran Manikandan | adiusted the vav temperature setpoint form 19c to 24c and damper position form 10% manual in bms system make it warm | [6 empty] | Aircon make it cool-mani-low
FID5290 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 8 > Delivery Suite 3 |  | 2022-01-01 07:56:48 | 2022-01-25 10:04:59 | 2022-01-25 10:05:41 | 2022-01-25 10:11:06 | 2022-01-25 10:11:26 | 2022-01-25 14:44:25 | FRC | Adjusted the aircon temperature setpoint make it warm in bms system | [6 empty] | Aircon make it warm -Aru-low
FID5289 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 7 > Operating Theatre 9 |  | 2022-01-01 07:53:41 | 2022-01-24 17:44:09 | 2022-01-24 17:44:31 | 2022-01-24 17:44:52 | 2022-01-24 17:45:13 | 2022-01-24 17:46:04 | FRC | Adjusted the temperature setpoint in bms system make it warm | [6 empty] | Aircon make it warm-aru-low
FID5288 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 13 > Ward 1328-1336 |  | 2022-01-01 07:47:55 | 2022-01-01 07:58:15 | 2022-01-01 08:17:21 | 2022-01-01 08:17:58 | 2022-01-01 08:18:41 | 2022-01-01 08:21:08 | Rajendran Manikandan | adiusted the vav temperature setpoint form 20c to 24c and damper position 5% manual in bms system make it warm | [6 empty] | Aircon make it warm -mani-low
FID5287 | Mechanical | AHU / FCU / CU | Too hot / Too cold | Localised to room | RMG > RH > 9 > Ward 916 |  | 2022-01-01 07:38:41 | 2022-01-24 17:33:30 | 2022-01-24 17:33:51 | 2022-01-24 17:34:14 | 2022-01-24 17:40:17 | 2022-01-24 17:41:29 | FRC | Adjusted the aircon temperature make it warm | [6 empty] | Aircon make it warm -aru-low
FID5286 | Electrical | Light Bulb | Flickering / Blown | Localised to room | RMG > RH > 5 > Carpark |  | 2022-01-01 07:33:26 | 2022-01-01 07:34:56 | 2022-01-01 07:39:44 | 2022-01-01 07:40:19 | 2022-01-01 07:41:03 | 2022-01-01 07:42:03 | Rajendran Manikandan | Replaced new bulb | [6 empty] | Light flickering-mani-low